## Костромаэнерго
[9 empty] | table 1 | [11 empty] | table 2
No. | Name of supply center, voltage class | Current deficit | [8 empty] | Note | No. | Name of supply center, voltage class | Expected deficit/proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Summary total capacity of supply centers following the results of measurements of load maximal Sмах | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transfer capacity, MVA | Current deficit/proficit MVA |  |  |  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Additional capacity according to provided technical specifications at TS, MVA | Expected load of Supply Center, MVA | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transfer capacity of Supply Center, MVA | Expected deficit/proficit, MVA
|  |  | MVA | MVA | Min | [11 empty] | MVA | Min
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
One-transformer substations | [11 empty] | 1: One-transformer substations
1 | Sandogora 35/6 kV | 1 | 0.47 | 0.55 | 120 | 0.55 | 0 | 0.55 | 0.08 | 0.08 | open | 1 | Sandogora 35/6 kV | 1 | 0.083 | 0.553 | 0.55 | 120 | 0.003 | 0 | 0.55 | -0.003 | -0.003 | closed
2 | Gridino 35/10 kV | 1.8 | 0.73 | 1.2 | 120 | 1.2 | 0 | 1.2 | 0.47 | 0.47 | open | 2 | Gridino 35/10 kV | 1.8 | 0.442 | 1.172 | 1.2 | 120 | -0.028 | 0 | 1.2 | 0.028 | 0.028 | open
3 | Novinki 35/10 kV | 1.8 | 0.15 | 1.44 | 120 | 1.44 | 0 | 1.44 | 1.29 | 1.29 | open | 3 | Novinki 35/10 kV | 1.8 | 0.329 | 0.479 | 1.44 | 120 | -0.961 | 0 | 1.44 | 0.961 | 0.961 | open
4 | Priskokovo 35/10kV | 2.5 | 1.5 | 1.5 | 120 | 1.5 | 0 | 1.5 | 0 | 0 | open | 4 | Priskokovo 35/10kV | 2.5 | 0.166 | 1.666 | 1.5 | 120 | 0.166 | 0 | 1.5 | -0.166 | -0.166 | closed
5 | Grigortsevo 110/10 kV | 2.5 | 0.25 | 1.5 | 120 | 1.5 | 0 | 1.5 | 1.25 | 1.25 | open | 5 | Grigortsevo 110/10 kV | 2.5 | 0 | 0.25 | 1.5 | 120 | -1.25 | 0 | 1.5 | 1.25 | 1.25 | open
6 | Klementyevo 110/10 kV | 6.3 | 0.47 | 3.7 | 120 | 3.7 | 0 | 3.7 | 3.23 | 3.23 | open | 6 | Klementyevo 110/10 kV | 6.3 | 0.065 | 0.535 | 3.7 | 120 | -3.165 | 0 | 3.7 | 3.165 | 3.165 | open
7 | Rudino 35/10 kV | 2.5 | 0.27 | 1.5 | 120 | 1.5 | 0 | 1.5 | 1.23 | 1.23 | open | 7 | Rudino 35/10 kV | 2.5 | 0.027 | 0.297 | 1.5 | 120 | -1.203 | 0 | 1.5 | 1.203 | 1.203 | open
8 | Stoyankovo 35/10 kV | 1.6 | 0.14 | 0.72 | 120 | 0.72 | 0 | 0.72 | 0.58 | 0.58 | open | 8 | Stoyankovo 35/10 kV | 1.6 | 0.075 | 0.215 | 0.72 | 120 | -0.505 | 0 | 0.72 | 0.505 | 0.505 | open
9 | Adishchevo 35/10 kV | 4 | 1.39 | 2.6 | 120 | 2.6 | 0 | 2.6 | 1.21 | 1.21 | open | 9 | Adishchevo 35/10 kV | 4 | 0.026 | 1.416 | 2.6 | 120 | -1.184 | 0 | 2.6 | 1.184 | 1.184 | open
10 | Stolbovo 110/10 kV | 10 | 0.27 | 4.6 | 120 | 4.6 | 0 | 4.6 | 4.33 | 4.33 | open | 10 | Stolbovo 110/10 kV | 10 | 0.011 | 0.281 | 4.6 | 120 | -4.319 | 0 | 4.6 | 4.319 | 4.319 | open
11 | Raslovo 35/10 kV | 2.5 | 0.62 | 1.38 | 120 | 1.38 | 0 | 1.38 | 0.76 | 0.76 | open | 11 | Raslovo 35/10 kV | 2.5 | 0.316 | 0.936 | 1.38 | 120 | -0.444 | 0 | 1.38 | 0.444 | 0.444 | open
12 | Andreevskoe 35/10 kV | 1.6 | 0.18 | 0.93 | 120 | 0.93 | 0 | 0.93 | 0.75 | 0.75 | open | 12 | Andreevskoe 35/10 kV | 1.6 | 0.03 | 0.21 | 0.93 | 120 | -0.72 | 0 | 0.93 | 0.72 | 0.72 | open
13 | Popadyino 35/10 kV | 1.6 | 0.22 | 0.88 | 120 | 0.88 | 0 | 0.88 | 0.66 | 0.66 | open | 13 | Popadyino 35/10 kV | 1.6 | 0.124 | 0.344 | 0.88 | 120 | -0.536 | 0 | 0.88 | 0.536 | 0.536 | open
14 | Elegino 110/10 kV | 2.5 | 0.21 | 0.98 | 120 | 0.98 | 0 | 0.98 | 0.77 | 0.77 | open | 14 | Elegino 110/10 kV | 2.5 | 0.234 | 0.444 | 0.98 | 120 | -0.536 | 0 | 0.98 | 0.536 | 0.536 | open
15 | Krenyovo 35/10 kV | 2.5 | 0.47 | 2.5 | 1 сутки | 2.5 | 0 | 2.5 | 2.03 | 2.03 | open | 15 | Krenyovo 35/10 kV | 2.5 | 0.059 | 0.529 | 2.5 | 1 сутки | -1.971 | 0 | 2.5 | 1.971 | 1.971 | open
16 | Semyonovskoe 35/10 kV | 1.6 | 0.2 | 1.6 | 1 сутки | 1.6 | 0 | 1.6 | 1.4 | 1.4 | open | 16 | Semyonovskoe 35/10 kV | 1.6 | 0 | 0.2 | 1.6 | 1 сутки | -1.4 | 0 | 1.6 | 1.4 | 1.4 | open
17 | Khimik 35/10 kV | 3.2 | 0.19 | 1.44 | 120 | 1.44 | 0 | 1.44 | 1.25 | 1.25 | open | 17 | Khimik 35/10 kV | 3.2 | 0 | 0.19 | 1.44 | 120 | -1.25 | 0 | 1.44 | 1.25 | 1.25 | open
18 | N. Beryozovets 35/10 kV | 2.5 | 0.33 | 0.43 | 120 | 0.43 | 0 | 0.43 | 0.1 | 0.1 | open | 18 | N. Beryozovets 35/10 kV | 2.5 | 0.028 | 0.358 | 0.43 | 120 | -0.072 | 0 | 0.43 | 0.072 | 0.072 | open
19 | Stepanovo 35/10 kV | 4 | 0.32 | 2.32 | 120 | 2.32 | 0 | 2.32 | 2 | 2 | open | 19 | Stepanovo 35/10 kV | 4 | 0.109 | 0.429 | 2.32 | 120 | -1.891 | 0 | 2.32 | 1.891 | 1.891 | open
20 | Gorbachevo 35/10 kV | 1 | 0.15 | 1.7 | 120 | 1.7 | 0 | 1.7 | 1.55 | 1.55 | open | 20 | Gorbachevo 35/10 kV | 1 | 0 | 0.15 | 1.7 | 120 | -1.55 | 0 | 1.7 | 1.55 | 1.55 | open
21 | Kalinino 35/10 kV | 1 | 0.13 | 0.56 | 120 | 0.56 | 0 | 0.56 | 0.43 | 0.43 | open | 21 | Kalinino 35/10 kV | 1 | 0 | 0.13 | 0.56 | 120 | -0.43 | 0 | 0.56 | 0.43 | 0.43 | open
22 | Kuzemino 35/10 kV | 1.6 | 0.28 | 1.6 | 1 сутки | 1.6 | 0 | 1.6 | 1.32 | 1.32 | open | 22 | Kuzemino 35/10 kV | 1.6 | 0 | 0.28 | 1.6 | 1 сутки | -1.32 | 0 | 1.6 | 1.32 | 1.32 | open
23 | Sovega 35/10 kV | 1 | 0.09 | 0.65 | 120 | 0.65 | 0 | 0.65 | 0.56 | 0.56 | open | 23 | Sovega 35/10 kV | 1 | 0 | 0.09 | 0.65 | 120 | -0.56 | 0 | 0.65 | 0.56 | 0.56 | open
24 | Lukovtsino 110/10 kV | 2.5 | 0.19 | 1.38 | 120 | 1.38 | 0 | 1.38 | 1.19 | 1.19 | open | 24 | Lukovtsino 110/10 kV | 2.5 | 0.006 | 0.196 | 1.38 | 120 | -1.184 | 0 | 1.38 | 1.184 | 1.184 | open
25 | Fyodorovskoe 110/10 kV | 2.5 | 0.15 | 1.5 | 120 | 1.5 | 0 | 1.5 | 1.35 | 1.35 | open | 25 | Fyodorovskoe 110/10 kV | 2.5 | 0.01 | 0.16 | 1.5 | 120 | -1.34 | 0 | 1.5 | 1.34 | 1.34 | open
26 | Pankratovo 35/10 kV | 1 | 0.06 | 0.39 | 120 | 0.39 | 0 | 0.39 | 0.33 | 0.33 | open | 26 | Pankratovo 35/10 kV | 1 | 0.034 | 0.094 | 0.39 | 120 | -0.296 | 0 | 0.39 | 0.296 | 0.296 | open
27 | Petrovskoe 35/10 kV | 1.6 | 0.32 | 0.77 | 120 | 0.77 | 0 | 0.77 | 0.45 | 0.45 | open | 27 | Petrovskoe 35/10 kV | 1.6 | 0.018 | 0.338 | 0.77 | 120 | -0.432 | 0 | 0.77 | 0.432 | 0.432 | open
28 | Kotelnikovo 35/10 kV | 1 | 0.13 | 0.26 | 120 | 0.26 | 0 | 0.26 | 0.13 | 0.13 | open | 28 | Kotelnikovo 35/10 kV | 1 | 0 | 0.13 | 0.26 | 120 | -0.13 | 0 | 0.26 | 0.13 | 0.13 | open
29 | Legitovo 35/10 kV | 2.5 | 0.37 | 1.1 | 120 | 1.1 | 0 | 1.1 | 0.73 | 0.73 | open | 29 | Legitovo 35/10 kV | 2.5 | 0 | 0.37 | 1.1 | 120 | -0.73 | 0 | 1.1 | 0.73 | 0.73 | open
30 | Sloboda 35/10 kV | 2.5 | 0.2 | 0.85 | 120 | 0.85 | 0 | 0.85 | 0.65 | 0.65 | open | 30 | Sloboda 35/10 kV | 2.5 | 0 | 0.2 | 0.85 | 120 | -0.65 | 0 | 0.85 | 0.65 | 0.65 | open
31 | Zavrazhye 35/10 kV | 1.6 | 0.29 | 0.74 | 120 | 0.74 | 0 | 0.74 | 0.45 | 0.45 | open | 31 | Zavrazhye 35/10 kV | 1.6 | 0.179 | 0.469 | 0.74 | 120 | -0.271 | 0 | 0.74 | 0.271 | 0.271 | open
32 | Okulovo 35/10 kV | 1.6 | 0.18 | 0.9 | 120 | 0.9 | 0 | 0.9 | 0.72 | 0.72 | open | 32 | Okulovo 35/10 kV | 1.6 | 0.186 | 0.366 | 0.9 | 120 | -0.534 | 0 | 0.9 | 0.534 | 0.534 | open
33 | Chernyshevo 35/10 kV | 4 | 0.57 | 1.8 | 120 | 1.8 | 0 | 1.8 | 1.23 | 1.23 | open | 33 | Chernyshevo 35/10 kV | 4 | 0.117 | 0.687 | 1.8 | 120 | -1.113 | 0 | 1.8 | 1.113 | 1.113 | open
34 | Yakovlevo 110/35/10 kV | 10 | 0.06 | 5.3 | 120 | 5.3 | 0 | 5.3 | 5.24 | 5.24 | open | 34 | Yakovlevo 110/35/10 kV | 10 | 0.006 | 0.066 | 5.3 | 120 | -5.234 | 0 | 5.3 | 5.234 | 5.234 | open
| Nom. Capacity MV, MVA | 10 | 0 | 0 | 120 | 0 | 0 | 0 | 0 |  |  |  | Nom. Capacity MV, MVA | 10 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0
| Nom. Capacity LV, MVA | 10 | 0.06 | 5.3 | 120 | 5.3 | 0 | 5.3 | 5.24 |  |  |  | Nom. Capacity LV, MVA | 10 | 0.006 | 0.066 | 5.3 | 120 | -5.234 | 0 | 5.3 | 5.234
35 | Chermenino 35/10 kV | 1.6 | 0.07 | 0.86 | 120 | 0.86 | 0 | 0.86 | 0.79 | 0.79 | open | 35 | Chermenino 35/10 kV | 1.6 | 0 | 0.07 | 0.86 | 120 | -0.79 | 0 | 0.86 | 0.79 | 0.79 | open
36 | Nezhitino 35/10 kV | 1 | 0.24 | 0.54 | 120 | 0.54 | 0 | 0.54 | 0.3 | 0.3 | open | 36 | Nezhitino 35/10 kV | 1 | 0.076 | 0.316 | 0.54 | 120 | -0.224 | 0 | 0.54 | 0.224 | 0.224 | open
37 | Nikolo-Makarovo 35/10 kV | 1.6 | 0.47 | 0.99 | 120 | 0.99 | 0 | 0.99 | 0.52 | 0.52 | open | 37 | Nikolo-Makarovo 35/10 kV | 1.6 | 0.164 | 0.634 | 0.99 | 120 | -0.356 | 0 | 0.99 | 0.356 | 0.356 | open
38 | Gusevo 110/10 kV | 2.5 | 0.29 | 1.63 | 120 | 1.63 | 0 | 1.63 | 1.34 | 1.34 | open | 38 | Gusevo 110/10 kV | 2.5 | 0.018 | 0.308 | 1.63 | 120 | -1.322 | 0 | 1.63 | 1.322 | 1.322 | open
39 | Medveditsa 35/10 kV | 2.5 | 0.53 | 1.3 | 120 | 1.3 | 0 | 1.3 | 0.77 | 0.77 | open | 39 | Medveditsa 35/10 kV | 2.5 | 0 | 0.53 | 1.3 | 120 | -0.77 | 0 | 1.3 | 0.77 | 0.77 | open
40 | Novinskoe 110/10 kV | 2.5 | 0.04 | 1.23 | 120 | 1.23 | 0 | 1.23 | 1.19 | 1.19 | open | 40 | Novinskoe 110/10 kV | 2.5 | 0 | 0.04 | 1.23 | 120 | -1.19 | 0 | 1.23 | 1.19 | 1.19 | open
41 | Filino 35/10 kV | 1.6 | 0.4 | 0.96 | 120 | 0.96 | 0 | 0.96 | 0.56 | 0.56 | open | 41 | Filino 35/10 kV | 1.6 | 0.122 | 0.522 | 0.96 | 120 | -0.438 | 0 | 0.96 | 0.438 | 0.438 | open
42 | Dyakonovo 110/10 kV | 2.5 | 0.28 | 1.13 | 120 | 1.13 | 0 | 1.13 | 0.85 | 0.85 | open | 42 | Dyakonovo 110/10 kV | 2.5 | 0 | 0.28 | 1.13 | 120 | -0.85 | 0 | 1.13 | 0.85 | 0.85 | open
43 | Oktyabrskaya 110/10 kV | 2.5 | 0.91 | 2.5 | 1 сутки | 2.5 | 0 | 2.5 | 1.59 | 1.59 | open | 43 | Oktyabrskaya 110/10 kV | 2.5 | 0.031 | 0.941 | 2.5 | 1 сутки | -1.559 | 0 | 2.5 | 1.559 | 1.559 | open
44 | Kuzhbal 35/10 kV | 2.5 | 0.4 | 1.48 | 120 | 1.48 | 0 | 1.48 | 1.08 | 1.08 | open | 44 | Kuzhbal 35/10 kV | 2.5 | 0.017 | 0.417 | 1.48 | 120 | -1.063 | 0 | 1.48 | 1.063 | 1.063 | open
45 | Nikolo-Poloma 110/10 kV | 2.5 | 1.04 | 1.13 | 120 | 1.13 | 0 | 1.13 | 0.09 | 0.09 | open | 45 | Nikolo-Poloma 110/10 kV | 2.5 | 0.079 | 1.119 | 1.13 | 120 | -0.011 | 0 | 1.13 | 0.011 | 0.011 | open
46 | Nikola 110/35/10 kV | 6.3 | 0.34 | 3.15 | 120 | 3.15 | 0 | 3.15 | 2.81 | 2.81 | open | 46 | Nikola 110/35/10 kV | 6.3 | 0.01 | 0.35 | 3.15 | 120 | -2.8 | 0 | 3.15 | 2.8 | 2.8 | open
| Nom. Capacity MV, MVA | 6.3 | 0 | 0 | 120 | 0 | 0 | 0 | 0 |  |  |  | Nom. Capacity MV, MVA | 6.3 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0
| Nom. Capacity LV, MVA | 6.3 | 0.34 | 3.15 | 120 | 3.15 | 0 | 3.15 | 2.81 |  |  |  | Nom. Capacity LV, MVA | 6.3 | 0.01 | 0.35 | 3.15 | 120 | -2.8 | 0 | 3.15 | 2.8
47 | Zavetluzhye 35/10 kV | 1.6 | 0.11 | 0.67 | 120 | 0.67 | 0 | 0.67 | 0.56 | 0.56 | open | 47 | Zavetluzhye 35/10 kV | 1.6 | 0 | 0.11 | 0.67 | 120 | -0.56 | 0 | 0.67 | 0.56 | 0.56 | open
48 | Talitsa 35/10 kV | 1.6 | 0.26 | 1.6 | 1 сутки | 1.6 | 0 | 1.6 | 1.34 | 1.34 | open | 48 | Talitsa 35/10 kV | 1.6 | 0 | 0.26 | 1.6 | 1 сутки | -1.34 | 0 | 1.6 | 1.34 | 1.34 | open
49 | Khoroshaya 35/10 kV | 2.5 | 0.06 | 1.95 | 120 | 1.95 | 0 | 1.95 | 1.89 | 1.89 | open | 49 | Khoroshaya 35/10 kV | 2.5 | 0 | 0.06 | 1.95 | 120 | -1.89 | 0 | 1.95 | 1.89 | 1.89 | open
50 | Zabegaevo 35/10 kV | 1.6 | 0.11 | 0.88 | 120 | 0.88 | 0 | 0.88 | 0.77 | 0.77 | open | 50 | Zabegaevo 35/10 kV | 1.6 | 0 | 0.11 | 0.88 | 120 | -0.77 | 0 | 0.88 | 0.77 | 0.77 | open
51 | Ilyinskoe 35/10 kV | 1.6 | 0.04 | 0.9 | 120 | 0.9 | 0 | 0.9 | 0.86 | 0.86 | open | 51 | Ilyinskoe 35/10 kV | 1.6 | 0 | 0.04 | 0.9 | 120 | -0.86 | 0 | 0.9 | 0.86 | 0.86 | open
52 | Luptyug 35/10 kV | 2.5 | 0.18 | 1.35 | 120 | 1.35 | 0 | 1.35 | 1.17 | 1.17 | open | 52 | Luptyug 35/10 kV | 2.5 | 0 | 0.18 | 1.35 | 120 | -1.17 | 0 | 1.35 | 1.17 | 1.17 | open
53 | Solovetskoe 35/10 kV | 1.6 | 0.09 | 0.72 | 120 | 0.72 | 0 | 0.72 | 0.63 | 0.63 | open | 53 | Solovetskoe 35/10 kV | 1.6 | 0 | 0.09 | 0.72 | 120 | -0.63 | 0 | 0.72 | 0.63 | 0.63 | open
54 | Gudkovo 110/10 kV | 2.5 | 0.06 | 1.38 | 120 | 1.38 | 0 | 1.38 | 1.32 | 1.32 | open | 54 | Gudkovo 110/10 kV | 2.5 | 0.037 | 0.097 | 1.38 | 120 | -1.283 | 0 | 1.38 | 1.283 | 1.283 | open
55 | Shortyug 110/10 kV | 6.3 | 0.52 | 3.47 | 120 | 3.47 | 0 | 3.47 | 2.95 | 2.95 | open | 55 | Shortyug 110/10 kV | 6.3 | 0.03 | 0.55 | 3.47 | 120 | -2.92 | 0 | 3.47 | 2.92 | 2.92 | open
56 | Yakshanga 110/10 kV | 6.3 | 1.41 | 3.47 | 120 | 3.47 | 0 | 3.47 | 2.06 | 2.06 | open | 56 | Yakshanga 110/10 kV | 6.3 | 0.083 | 1.493 | 3.47 | 120 | -1.977 | 0 | 3.47 | 1.977 | 1.977 | open
57 | Katunino 35/10 kV | 2.5 | 0.17 | 1.33 | 120 | 1.33 | 0 | 1.33 | 1.16 | 1.16 | open | 57 | Katunino 35/10 kV | 2.5 | 0 | 0.17 | 1.33 | 120 | -1.16 | 0 | 1.33 | 1.16 | 1.16 | open
58 | Konyovo 35/10 kV | 1.6 | 0.33 | 0.88 | 120 | 0.88 | 0 | 0.88 | 0.55 | 0.55 | open | 58 | Konyovo 35/10 kV | 1.6 | 0.029 | 0.359 | 0.88 | 120 | -0.521 | 0 | 0.88 | 0.521 | 0.521 | open
59 | Shekshema 110/10 kV | 6.3 | 0.58 | 2.5 | 1 сутки | 2.5 | 0 | 2.5 | 1.92 | 1.92 | open | 59 | Shekshema 110/10 kV | 6.3 | 0.052 | 0.632 | 2.5 | 1 сутки | -1.868 | 0 | 2.5 | 1.868 | 1.868 | open
60 | Golovino 35/10 kV | 1 | 0.06 | 0.12 | 120 | 0.12 | 0 | 0.12 | 0.06 | 0.06 | open | 60 | Golovino 35/10 kV | 1 | 0 | 0.06 | 0.12 | 120 | -0.06 | 0 | 0.12 | 0.06 | 0.06 | open
61 | Pishchyovka 35/10 kV | 1 | 0.19 | 0.45 | 120 | 0.45 | 0 | 0.45 | 0.26 | 0.26 | open | 61 | Pishchyovka 35/10 kV | 1 | 0.08 | 0.27 | 0.45 | 120 | -0.18 | 0 | 0.45 | 0.18 | 0.18 | open
Two- and more transformer substations | [11 empty] | 1: Two- and more transformer substations
62 | Vasilyovo 110/35/10 kV | 10+10 | 2.13 | 0.86 | 120 | 1.27 | 0 | 10.5 | 9.23 | 9.23 | open | 62 | Vasilyovo 110/35/10 kV | 10+10 | 3.974 | 6.104 | 0.86 | 120 | 5.244 | 0 | 10.5 | 5.256 | 5.256 | open
| Nom. Capacity MV, MVA | 10+10 | 0.59 | 0 | 120 | 0.59 | 0 | 10.5 | 9.91 |  |  |  | Nom. Capacity MV, MVA | 10+10 | 0 | 0.59 | 0 | 120 | 0.59 | 0 | 10.5 | 9.91
| Nom. Capacity LV, MVA | 10+10 | 1.54 | 0.86 | 120 | 0.68 | 0 | 10.5 | 9.82 |  |  |  | Nom. Capacity LV, MVA | 10+10 | 3.974 | 5.514 | 0.86 | 120 | 4.654 | 0 | 10.5 | 5.846
63 | Kalinki 110/35/10/6 kV | 10+10+1,6 | 6.12 | 1.15 | 120 | 4.97 | 0 | 12.18 | 7.21 | 7.21 | open | 63 | Kalinki 110/35/10/6 kV | 10+10+1,6 | 0.43 | 6.55 | 1.15 | 120 | 5.4 | 0 | 12.18 | 6.78 | 6.78 | open
| Nom. Capacity MV, MVA | 10+10+1,6 | 4.59 | 0 | 120 | 4.59 | 0 | 12.18 | 7.59 |  |  |  | Nom. Capacity MV, MVA | 10+10+1,6 | 0 | 4.59 | 0 | 120 | 4.59 | 0 | 12.18 | 7.59
| Nom. Capacity LV, MVA | 10+10+1,6 | 1.53 | 1.15 | 120 | 0.38 | 0 | 12.18 | 11.8 |  |  |  | Nom. Capacity LV, MVA | 10+10+1,6 | 0.43 | 1.96 | 1.15 | 120 | 0.81 | 0 | 12.18 | 11.37
64 | Apraksino 35/10 kV | 2,5+2,5 | 1.73 | 0.425 | 120 | 1.305 | 0 | 2.625 | 1.32 | 1.32 | open | 64 | Apraksino 35/10 kV | 2,5+2,5 | 0.873 | 2.603 | 0.425 | 120 | 2.178 | 0 | 2.625 | 0.447 | 0.447 | open
65 | Borshchino 35/10 kV | 4+4 | 0.63 | 0.62 | 120 | 0.01 | 0 | 4.2 | 4.19 | 4.19 | open | 65 | Borshchino 35/10 kV | 4+4 | 0.548 | 1.178 | 0.62 | 120 | 0.558 | 0 | 4.2 | 3.642 | 3.642 | open
66 | Gorkovskaya 35/10 kV | 1,6+1,6 | 0.2 | 0.11 | 120 | 0.09 | 0 | 1.68 | 1.59 | 1.59 | open | 66 | Gorkovskaya 35/10 kV | 1,6+1,6 | 0.014 | 0.214 | 0.11 | 120 | 0.104 | 0 | 1.68 | 1.576 | 1.576 | open
67 | Ilyinskoe 35/10 kV | 2,5+2,5 | 2.33 | 0.55 | 120 | 1.78 | 0 | 2.625 | 0.845 | 0.845 | open | 67 | Ilyinskoe 35/10 kV | 2,5+2,5 | 0.556 | 2.886 | 0.55 | 120 | 2.336 | 0 | 2.625 | 0.289 | 0.289 | open
68 | Kuznetsovo 35/10 kV | 2,5+2,5 | 1.18 | 0.4 | 120 | 0.78 | 0 | 2.625 | 1.845 | 1.845 | open | 68 | Kuznetsovo 35/10 kV | 2,5+2,5 | 0.38 | 1.56 | 0.4 | 120 | 1.16 | 0 | 2.625 | 1.465 | 1.465 | open
69 | Kuzmishchi 35/10 kV | 1,6+1,6 | 0.74 | 0.29 | 120 | 0.45 | 0 | 1.68 | 1.23 | 1.23 | open | 69 | Kuzmishchi 35/10 kV | 1,6+1,6 | 0.142 | 0.882 | 0.29 | 120 | 0.592 | 0 | 1.68 | 1.088 | 1.088 | open
70 | Minskoe 35/10 kV | 2,5+2,5 | 1.3 | 0.43 | 120 | 0.87 | 0 | 2.625 | 1.755 | 1.755 | open | 70 | Minskoe 35/10 kV | 2,5+2,5 | 0.669 | 1.969 | 0.43 | 120 | 1.539 | 0 | 2.625 | 1.086 | 1.086 | open
71 | Miskovo 35/6 kV | 1,8+1,8 | 0.36 | 0.2 | 120 | 0.16 | 0 | 1.89 | 1.73 | 1.73 | open | 71 | Miskovo 35/6 kV | 1,8+1,8 | 0.124 | 0.484 | 0.2 | 120 | 0.284 | 0 | 1.89 | 1.606 | 1.606 | open
72 | Nikolskoe 35/6 kV | 4+4 | 2.5 | 0.92 | 120 | 1.58 | 0 | 4.2 | 2.62 | 2.62 | open | 72 | Nikolskoe 35/6 kV | 4+4 | 0.776 | 3.276 | 0.92 | 120 | 2.356 | 0 | 4.2 | 1.844 | 1.844 | open
73 | Samet 35/6 kV | 1,6+4 | 1.43 | 0 | 0 | 1.43 | 0 | 1.68 | 0.25 | 0.25 | open | 73 | Samet 35/6 kV | 1,6+4 | 0.191 | 1.621 | 0 | 0 | 1.621 | 0 | 1.68 | 0.059 | 0.059 | open
74 | Sukhonogovo 35/10 kV | 3,2+4 | 2.71 | 0 | 0 | 2.71 | 0 | 3.36 | 0.65 | 0.65 | open | 74 | Sukhonogovo 35/10 kV | 3,2+4 | 1.022 | 3.732 | 0 | 0 | 3.732 | 0 | 3.36 | -0.372 | -0.372 | closed
75 | Sushchevo 35/10 kV | 4+4 | 3.68 | 0.76 | 120 | 2.92 | 0 | 4.2 | 1.28 | 1.28 | open | 75 | Sushchevo 35/10 kV | 4+4 | 0.524 | 4.204 | 0.76 | 120 | 3.444 | 0 | 4.2 | 0.756 | 0.756 | open
76 | EMZ 35/6 kV | 1+1 | 0.82 | 0 | 0 | 0.82 | 0 | 1.05 | 0.23 | 0.23 | open | 76 | EMZ 35/6 kV | 1+1 | 0 | 0.82 | 0 | 0 | 0.82 | 0 | 1.05 | 0.23 | 0.23 | open
77 | Krasnoe 110/35/10 kV | 16+16 | 12.41 | 0 | 0 | 12.41 | 0 | 16.8 | 4.39 | 4.39 | open | 77 | Krasnoe 110/35/10 kV | 16+16 | 2.173 | 14.583 | 0 | 0 | 14.583 | 0 | 16.8 | 2.217 | 2.217 | open
| Nom. Capacity MV, MVA | 16+16 | 0.77 | 0 | 0 | 0.77 | 0 | 16.8 | 16.03 |  |  |  | Nom. Capacity MV, MVA | 16+16 | 0 | 0.77 | 0 | 0 | 0.77 | 0 | 16.8 | 16.03
| Nom. Capacity LV, MVA | 16+16 | 11.64 | 0 | 0 | 11.64 | 0 | 16.8 | 5.16 |  |  |  | Nom. Capacity LV, MVA | 16+16 | 2.173 | 13.813 | 0 | 0 | 13.813 | 0 | 16.8 | 2.987
78 | Isaevo 35/10 kV | 4+4 | 1.65 | 1.03 | 120 | 0.62 | 0 | 4.2 | 3.58 | 3.58 | open | 78 | Isaevo 35/10 kV | 4+4 | 2.733 | 4.383 | 1.03 | 120 | 3.353 | 0 | 4.2 | 0.847 | 0.847 | open
79 | Chapaevo 35/10 kV | 2,5+2,5 | 1.27 | 0.43 | 120 | 0.84 | 0 | 2.625 | 1.785 | 1.785 | open | 79 | Chapaevo 35/10 kV | 2,5+2,5 | 0.197 | 1.467 | 0.43 | 120 | 1.037 | 0 | 2.625 | 1.588 | 1.588 | open
80 | Chernevo 35/10 kV | 1,8+1,8 | 0.37 | 0.43 | 120 | -0.06 | 0 | 1.89 | 1.95 | 1.95 | open | 80 | Chernevo 35/10 kV | 1,8+1,8 | 0.01 | 0.38 | 0.43 | 120 | -0.05 | 0 | 1.89 | 1.94 | 1.94 | open
81 | Nerekhta-1 110/35/10 kV | 25+25 | 18.51 | 2.75 | 120 | 15.76 | 0 | 26.25 | 10.49 | 10.49 | open | 81 | Nerekhta-1 110/35/10 kV | 25+25 | 0.847 | 19.357 | 2.75 | 120 | 16.607 | 0 | 26.25 | 9.643 | 9.643 | open
| Nom. Capacity MV, MVA | 25+25 | 6.52 | 0 | 120 | 6.52 | 0 | 26.25 | 19.73 |  |  |  | Nom. Capacity MV, MVA | 25+25 | 0 | 6.52 | 0 | 120 | 6.52 | 0 | 26.25 | 19.73
| Nom. Capacity LV, MVA | 25+25 | 11.99 | 2.75 | 120 | 9.24 | 0 | 26.25 | 17.01 |  |  |  | Nom. Capacity LV, MVA | 25+25 | 0.847 | 12.837 | 2.75 | 120 | 10.087 | 0 | 26.25 | 16.163
| Nerekhta-1 110/10 kV | 16+16 | 5.79 | 2.2 | 120 | 3.59 | 0 | 16.8 | 13.21 |  |  |  | Nerekhta-1 110/10 kV | 16+16 | 0 | 5.79 | 2.2 | 120 | 3.59 | 0 | 16.8 | 13.21
82 | Nerekhta-2 110/10/6 kV | 5,6+10 | 0.93 | 1.55 | 120 | -0.62 | 0 | 5.88 | 6.5 | 6.5 | open | 82 | Nerekhta-2 110/10/6 kV | 10+10 | 5.822 | 6.752 | 1.55 | 120 | 5.202 | 0 | 10.5 | 5.298 | 5.298 | open
83 | Vladychnoe 35/10 kV | 1,6+1,6 | 0.7 | 0.41 | 120 | 0.29 | 0 | 1.68 | 1.39 | 1.39 | open | 83 | Vladychnoe 35/10 kV | 1,6+1,6 | 0.105 | 0.805 | 0.41 | 120 | 0.395 | 0 | 1.68 | 1.285 | 1.285 | open
84 | Tatarskoe 35/10 kV | 1,6+1,6 | 0.38 | 0.23 | 120 | 0.15 | 0 | 1.68 | 1.53 | 1.53 | open | 84 | Tatarskoe 35/10 kV | 1,6+1,6 | 0.002 | 0.382 | 0.23 | 120 | 0.152 | 0 | 1.68 | 1.528 | 1.528 | open
85 | Aleksandrovo 110/35/10 kV | 6,3+6,3 | 4 | 0.76 | 120 | 3.24 | 0 | 6.615 | 3.375 | 3.375 | open | 85 | Aleksandrovo 110/35/10 kV | 6,3+6,3 | 0.082 | 4.082 | 0.76 | 120 | 3.322 | 0 | 6.615 | 3.293 | 3.293 | open
| Nom. Capacity MV, MVA | 6,3+6,3 | 0.3 | 0 | 120 | 0.3 | 0 | 6.615 | 6.315 |  |  |  | Nom. Capacity MV, MVA | 6,3+6,3 | 0 | 0.3 | 0 | 120 | 0.3 | 0 | 6.615 | 6.315
| Nom. Capacity LV, MVA | 6,3+6,3 | 3.7 | 0.76 | 120 | 2.94 | 0 | 6.615 | 3.675 |  |  |  | Nom. Capacity LV, MVA | 6,3+6,3 | 0.082 | 3.782 | 0.76 | 120 | 3.022 | 0 | 6.615 | 3.593
86 | Krasnaya Polyana 110/35/10 kV | 10+10 | 3.91 | 1.28 | 120 | 2.63 | 0 | 10.5 | 7.87 | 7.87 | open | 86 | Krasnaya Polyana 110/35/10 kV | 10+10 | 1.26 | 5.17 | 1.28 | 120 | 3.89 | 0 | 10.5 | 6.61 | 6.61 | open
| Nom. Capacity MV, MVA | 10+10 | 0.72 | 0 | 120 | 0.72 | 0 | 10.5 | 9.78 |  |  |  | Nom. Capacity MV, MVA | 10+10 | 0 | 0.72 | 0 | 120 | 0.72 | 0 | 10.5 | 9.78
| Nom. Capacity LV, MVA | 10+10 | 3.19 | 1.28 | 120 | 1.91 | 0 | 10.5 | 8.59 |  |  |  | Nom. Capacity LV, MVA | 10+10 | 1.26 | 4.45 | 1.28 | 120 | 3.17 | 0 | 10.5 | 7.33
87 | Igodovo 35/10 kV | 1,6+1,6 | 0.37 | 0.25 | 120 | 0.12 | 0 | 1.68 | 1.56 | 1.56 | open | 87 | Igodovo 35/10 kV | 1,6+1,6 | 0.096 | 0.466 | 0.25 | 120 | 0.216 | 0 | 1.68 | 1.464 | 1.464 | open
88 | Klevantsovo 35/10 kV | 1,6+1,6 | 0.8 | 0.56 | 120 | 0.24 | 0 | 1.68 | 1.44 | 1.44 | open | 88 | Klevantsovo 35/10 kV | 1,6+1,6 | 0.028 | 0.828 | 0.56 | 120 | 0.268 | 0 | 1.68 | 1.412 | 1.412 | open
89 | Ostrovskoe 35/10 kV | 2,5+2,5 | 1.32 | 0.52 | 120 | 0.8 | 0 | 2.625 | 1.825 | 1.825 | open | 89 | Ostrovskoe 35/10 kV | 2,5+2,5 | 0.078 | 1.398 | 0.52 | 120 | 0.878 | 0 | 2.625 | 1.747 | 1.747 | open
90 | Sudislavl 110/10 kV | 10+10 | 8.14 | 1.8 | 120 | 6.34 | 0 | 10.5 | 4.16 | 4.16 | open | 90 | Sudislavl 110/10 kV | 10+10 | 1.39 | 9.53 | 1.8 | 120 | 7.73 | 0 | 10.5 | 2.77 | 2.77 | open
91 | Voronye 35/10 kV | 1,8+1,8 | 0.49 | 0.4 | 120 | 0.09 | 0 | 1.89 | 1.8 | 1.8 | open | 91 | Voronye 35/10 kV | 1,8+1,8 | 0.082 | 0.572 | 0.4 | 120 | 0.172 | 0 | 1.89 | 1.718 | 1.718 | open
92 | Susanino 110/35/10 kV | 10+10 | 3.93 | 1.89 | 120 | 2.04 | 0 | 10.5 | 8.46 | 8.46 | open | 92 | Susanino 110/35/10 kV | 10+10 | 0.588 | 4.518 | 1.89 | 120 | 2.628 | 0 | 10.5 | 7.872 | 7.872 | open
| Nom. Capacity MV, MVA | 10+10 | 0.38 | 0 | 120 | 0.38 | 0 | 10.5 | 10.12 |  |  |  | Nom. Capacity MV, MVA | 10+10 | 0 | 0.38 | 0 | 120 | 0.38 | 0 | 10.5 | 10.12
| Nom. Capacity LV, MVA | 10+10 | 3.55 | 1.89 | 120 | 1.66 | 0 | 10.5 | 8.84 |  |  |  | Nom. Capacity LV, MVA | 10+10 | 0.588 | 4.138 | 1.89 | 120 | 2.248 | 0 | 10.5 | 8.252
93 | Kaliniskaya 35/10 kV | 2,5+2,5 | 0.25 | 0.07 | 120 | 0.18 | 0 | 2.625 | 2.445 | 2.445 | open | 93 | Kaliniskaya 35/10 kV | 2,5+2,5 | 0.025 | 0.275 | 0.07 | 120 | 0.205 | 0 | 2.625 | 2.42 | 2.42 | open
94 | Airport 110/35/6 kV | 16+16 | 5.39 | 2.88 | 120 | 2.51 | 0 | 16.8 | 14.29 | 14.29 | open | 94 | Airport 110/35/6 kV | 16+16 | 10.108 | 15.498 | 2.88 | 120 | 12.618 | 0 | 16.8 | 4.182 | 4.182 | open
| Nom. Capacity MV, MVA | 16+16 | 0 | 0 | 120 | 0 | 0 | 16.8 | 16.8 |  |  |  | Nom. Capacity MV, MVA | 16+16 | 0 | 0 | 0 | 120 | 0 | 0 | 16.8 | 16.8
| Nom. Capacity LV, MVA | 16+16 | 5.39 | 2.88 | 120 | 2.51 | 0 | 16.8 | 14.29 |  |  |  | Nom. Capacity LV, MVA | 16+16 | 10.108 | 15.498 | 2.88 | 120 | 12.618 | 0 | 16.8 | 4.182
95 | Vostochnaya-2 110/35/10 kV | 25+25 | 23.04 | 0.02 | 120 | 23.02 | 0 | 26.25 | 3.23 | 3.23 | open | 95 | Vostochnaya-2 110/35/10 kV | 25+25 | 3.11 | 26.15 | 0.02 | 120 | 26.13 | 0 | 26.25 | 0.12 | 0.12 | open
| Nom. Capacity MV, MVA | 25+25 | 19.24 | 0 | 120 | 19.24 | 0 | 26.25 | 7.01 |  |  |  | Nom. Capacity MV, MVA | 25+25 | 0 | 19.24 | 0 | 120 | 19.24 | 0 | 26.25 | 7.01
| Nom. Capacity LV, MVA | 25+25 | 3.8 | 0.02 | 120 | 3.78 | 0 | 26.25 | 22.47 |  |  |  | Nom. Capacity LV, MVA | 25+25 | 3.11 | 6.91 | 0.02 | 120 | 6.89 | 0 | 26.25 | 19.36
96 | Kostroma-3 110/35/10 kV | 10+16 | 11.49 | 0 | 120 | 11.49 | 0 | 10.5 | -0.99 | -0.99 | closed | 96 | Kostroma-3 110/35/10 kV | 10+16 | 1.987 | 13.477 | 0 | 120 | 13.477 | 0 | 10.5 | -2.977 | -2.977 | closed
| Nom. Capacity MV, MVA | 10+16 | 2.68 | 0 | 120 | 2.68 | 0 | 10.5 | 7.82 |  |  |  | Nom. Capacity MV, MVA | 10+16 | 0 | 2.68 | 0 | 120 | 2.68 | 0 | 10.5 | 7.82
| Nom. Capacity LV, MVA | 10+16 | 8.81 | 0 | 120 | 8.81 | 0 | 10.5 | 1.69 |  |  |  | Nom. Capacity LV, MVA | 10+16 | 1.987 | 10.797 | 0 | 120 | 10.797 | 0 | 10.5 | -0.297
97 | Yuzhnaya 110/35/10 kV | 25+25 | 13.975 | 0 | 120 | 13.975 | 0 | 26.25 | 12.275 | 12.275 | open | 97 | Yuzhnaya 110/35/10 kV | 25+25 | 7.626 | 21.601 | 0 | 120 | 21.601 | 0 | 26.25 | 4.649 | 4.649 | open
| Nom. Capacity MV, MVA | 25+25 | 4.35 | 0 | 120 | 4.35 | 0 | 26.25 | 21.9 |  |  |  | Nom. Capacity MV, MVA | 25+25 | 0 | 4.35 | 0 | 120 | 4.35 | 0 | 26.25 | 21.9
| Nom. Capacity LV, MVA | 25+25 | 9.625 | 0 | 120 | 9.625 | 0 | 26.25 | 16.625 |  |  |  | Nom. Capacity LV, MVA | 25+25 | 7.626 | 17.251 | 0 | 120 | 17.251 | 0 | 26.25 | 8.999
98 | Davydovskaya 110/10 kV | 25+25 | 8.91 | 0.02 | 120 | 8.89 | 0 | 26.25 | 17.36 | 17.36 | open | 98 | Davydovskaya 110/10 kV | 25+25 | 3.131 | 12.041 | 0.02 | 120 | 12.021 | 0 | 26.25 | 14.229 | 14.229 | open | commisioned 09.2009
99 | Kostroma-1 110/6 kV | 10+10 | 10.38 | 0 | 0 | 10.38 | 0 | 10.5 | 0.12 | 0.12 | open | 99 | Kostroma-1 110/6 kV | 10+10 | 1.116 | 11.496 | 0 | 0 | 11.496 | 0 | 10.5 | -0.996 | -0.996 | closed
100 | Severnaya 110/6 kV | 20+25 | 19.24 | 0 | 0 | 19.24 | 0 | 21 | 1.76 | 1.76 | open | 100 | Severnaya 110/6 kV | 20+25 | 2.218 | 21.458 | 0 | 0 | 21.458 | 0 | 21 | -0.458 | -0.458 | closed
101 | Strommashina 110/6 kV | 40+40 | 13.83 | 0 | 0 | 13.83 | 0 | 42 | 28.17 | 28.17 | open | 101 | Strommashina 110/6 kV | 40+40 | 4.542 | 18.372 | 0 | 0 | 18.372 | 0 | 42 | 23.628 | 23.628 | open
102 | Tsentralnaya 110/10/6 kV | 25+25 | 16.44 | 0 | 0 | 16.44 | 0 | 26.25 | 9.81 | 9.81 | open | 102 | Tsentralnaya 110/10/6 kV | 25+25 | 6.978 | 23.418 | 0 | 0 | 23.418 | 0 | 26.25 | 2.832 | 2.832 | open
103 | Baydarka 35/6 kV | 6,3+6,3 | 1.99 | 1.2 | 120 | 0.79 | 0 | 6.615 | 5.825 | 5.825 | open | 103 | Baydarka 35/6 kV | 6,3+6,3 | 0.84 | 2.83 | 1.2 | 120 | 1.63 | 0 | 6.615 | 4.985 | 4.985 | open
104 | Volzhskaya 35/6 kV | 4+4 | 1.29 | 0.76 | 120 | 0.53 | 0 | 4.2 | 3.67 | 3.67 | open | 104 | Volzhskaya 35/6 kV | 4+4 | 0.583 | 1.873 | 0.76 | 120 | 1.113 | 0 | 4.2 | 3.087 | 3.087 | open
105 | Vostochnaya-1 35/6 kV | 10+10+6,3 | 22.36 | 0 | 0 | 22.36 | 0 | 17.115 | -5.245 | -5.245 | closed | 105 | Vostochnaya-1 35/6 kV | 10+10+6,3 | 2.512 | 24.872 | 0 | 0 | 24.872 | 0 | 17.115 | -7.757 | -7.757 | closed
106 | Karavaevo 35/10 kV | 6,3+6,3 | 3.46 | 0 | 0 | 3.46 | 0 | 6.615 | 3.155 | 3.155 | open | 106 | Karavaevo 35/10 kV | 6,3+6,3 | 1.626 | 5.086 | 0 | 0 | 5.086 | 0 | 6.615 | 1.529 | 1.529 | open
107 | Korkino 35/10 kV | 2,5+2,5 | 1.73 | 0.85 | 120 | 0.88 | 0 | 2.625 | 1.745 | 1.745 | open | 107 | Korkino 35/10 kV | 2,5+2,5 | 0.421 | 2.151 | 0.85 | 120 | 1.301 | 0 | 2.625 | 1.324 | 1.324 | open
108 | KPD 110/35/10 kV | 16+16 | 7.54 | 1.44 | 120 | 6.1 | 0 | 16.8 | 10.7 | 10.7 | open | 108 | KPD 110/35/10 kV | 16+16 | 11.047 | 18.587 | 1.44 | 120 | 17.147 | 0 | 16.8 | -0.347 | -0.347 | closed
| Nom. Capacity MV, MVA | 16+16 | 0.62 | 0 | 120 | 0.62 | 0 | 16.8 | 16.18 |  |  |  | Nom. Capacity MV, MVA | 16+16 | 0 | 0.62 | 0 | 120 | 0.62 | 0 | 16.8 | 16.18
| Nom. Capacity LV, MVA | 16+16 | 6.92 | 1.44 | 120 | 5.48 | 0 | 16.8 | 11.32 |  |  |  | Nom. Capacity LV, MVA | 16+16 | 11.047 | 17.967 | 1.44 | 120 | 16.527 | 0 | 16.8 | 0.273
109 | SM State district power station 110/35/6 kV | 10+16 | 6.48 | 0 | 0 | 6.48 | 0 | 10.5 | 4.02 | 4.02 | open | 109 | SM State district power station 110/35/6 kV | 10+16 | 2.015 | 8.495 | 0 | 0 | 8.495 | 0 | 10.5 | 2.005 | 2.005 | open
| Nom. Capacity MV, MVA | 10+16 | 0.62 | 0 | 0 | 0.62 | 0 | 10.5 | 9.88 |  |  |  | Nom. Capacity MV, MVA | 10+16 | 0 | 0.62 | 0 | 0 | 0.62 | 0 | 10.5 | 9.88
| Nom. Capacity LV, MVA | 10+16 | 5.86 | 0 | 0 | 5.86 | 0 | 10.5 | 4.64 |  |  |  | Nom. Capacity LV, MVA | 10+16 | 2.015 | 7.875 | 0 | 0 | 7.875 | 0 | 10.5 | 2.625
110 | Sidorovskoe 35/6 kV | 2,5+4 | 0.76 | 0.88 | 120 | -0.12 | 0 | 2.625 | 2.745 | 2.745 | open | 110 | Sidorovskoe 35/6 kV | 2,5+4 | 0.645 | 1.405 | 0.88 | 120 | 0.525 | 0 | 2.625 | 2.1 | 2.1 | open
111 | Buy (r) 110/35/10 kV | 4+10 | 1.87 | 0 | 120 | 1.87 | 0 | 4.2 | 2.33 | 2.33 | open | 111 | Buy (r) 110/35/10 kV | 4+10 | 0.419 | 2.289 | 0 | 120 | 2.289 | 0 | 4.2 | 1.911 | 1.911 | open
| Nom. Capacity MV, MVA | 4+10 | 1.87 | 0 | 120 | 1.87 | 0 | 4.2 | 2.33 |  |  |  | Nom. Capacity MV, MVA | 4+10 | 0 | 1.87 | 0 | 120 | 1.87 | 0 | 4.2 | 2.33
| Nom. Capacity LV, MVA | 4+10 | 0 | 0 | 120 | 0 | 0 | 4.2 | 4.2 |  |  |  | Nom. Capacity LV, MVA | 4+10 | 0.419 | 0.419 | 0 | 120 | 0.419 | 0 | 4.2 | 3.781
112 | Buy (agriculture) 110/10 kV | 6,3+6,3 | 6.25 | 1.2 | 120 | 5.05 | 0 | 6.615 | 1.565 | 1.565 | open | 112 | Buy (agriculture) 110/10 kV | 6,3+6,3 | 0.782 | 7.032 | 1.2 | 120 | 5.832 | 0 | 6.615 | 0.783 | 0.783 | open
113 | Zapadnaya 110/10 kV | 10+10 | 5.84 | 2.63 | 120 | 3.21 | 0 | 10.5 | 7.29 | 7.29 | open | 113 | Zapadnaya 110/10 kV | 10+10 | 0.024 | 5.864 | 2.63 | 120 | 3.234 | 0 | 10.5 | 7.266 | 7.266 | open
114 | Dor 35/10 kV | 1,6+1,6 | 0.46 | 0.06 | 120 | 0.4 | 0 | 1.68 | 1.28 | 1.28 | open | 114 | Dor 35/10 kV | 1,6+1,6 | 0.023 | 0.483 | 0.06 | 120 | 0.423 | 0 | 1.68 | 1.257 | 1.257 | open
115 | Dyakonovo 35/10 kV | 1+1 | 0.23 | 0.26 | 120 | -0.03 | 0 | 1.05 | 1.08 | 1.08 | open | 115 | Dyakonovo 35/10 kV | 1+1 | 0 | 0.23 | 0.26 | 120 | -0.03 | 0 | 1.05 | 1.08 | 1.08 | open
116 | Likurga 35/10 kV | 1,8+1,6 | 0.2 | 0.12 | 120 | 0.08 | 0 | 1.68 | 1.6 | 1.6 | open | 116 | Likurga 35/10 kV | 1,8+1,6 | 0.001 | 0.201 | 0.12 | 120 | 0.081 | 0 | 1.68 | 1.599 | 1.599 | open
117 | Shushkodom 35/10 kV | 1+1 | 0.29 | 0.06 | 120 | 0.23 | 0 | 1.05 | 0.82 | 0.82 | open | 117 | Shushkodom 35/10 kV | 1+1 | 0.018 | 0.308 | 0.06 | 120 | 0.248 | 0 | 1.05 | 0.802 | 0.802 | open
118 | Novaya 110/35/10 kV | 6,3+6,3 | 2.93 | 0.64 | 120 | 2.29 | 0 | 6.615 | 4.325 | 4.325 | open | 118 | Novaya 110/35/10 kV | 6,3+6,3 | 0.712 | 3.642 | 0.64 | 120 | 3.002 | 0 | 6.615 | 3.613 | 3.613 | open
| Nom. Capacity MV, MVA | 6,3+6,3 | 1.83 | 0 | 120 | 1.83 | 0 | 6.615 | 4.785 |  |  |  | Nom. Capacity MV, MVA | 6,3+6,3 | 0 | 1.83 | 0 | 120 | 1.83 | 0 | 6.615 | 4.785
| Nom. Capacity LV, MVA | 6,3+6,3 | 1.1 | 0.64 | 120 | 0.46 | 0 | 6.615 | 6.155 |  |  |  | Nom. Capacity LV, MVA | 6,3+6,3 | 0.712 | 1.812 | 0.64 | 120 | 1.172 | 0 | 6.615 | 5.443
119 | Orekhovo 110/35/10 kV | 6,3+6,3 | 1.36 | 0 | 120 | 1.36 | 0 | 6.615 | 5.255 | 5.255 | open | 119 | Orekhovo 110/35/10 kV | 6,3+6,3 | 0.172 | 1.532 | 0 | 120 | 1.532 | 0 | 6.615 | 5.083 | 5.083 | open
| Nom. Capacity MV, MVA | 6,3+6,3 | 0.53 | 0 | 120 | 0.53 | 0 | 6.615 | 6.085 |  |  |  | Nom. Capacity MV, MVA | 6,3+6,3 | 0 | 0.53 | 0 | 120 | 0.53 | 0 | 6.615 | 6.085
| Nom. Capacity LV, MVA | 6,3+6,3 | 0.83 | 0 | 120 | 0.83 | 0 | 6.615 | 5.785 |  |  |  | Nom. Capacity LV, MVA | 6,3+6,3 | 0.172 | 1.002 | 0 | 120 | 1.002 | 0 | 6.615 | 5.613
120 | Loparevo 110/10 kV | 2,5+2,5 | 0.61 | 0.55 | 120 | 0.06 | 0 | 2.625 | 2.565 | 2.565 | open | 120 | Loparevo 110/10 kV | 2,5+2,5 | 0.227 | 0.837 | 0.55 | 120 | 0.287 | 0 | 2.625 | 2.338 | 2.338 | open
121 | Poultry farm 35/10 kV | 4+4 | 1.73 | 1.28 | 120 | 0.45 | 0 | 4.2 | 3.75 | 3.75 | open | 121 | Poultry farm 35/10 kV | 4+4 | 0.03 | 1.76 | 1.28 | 120 | 0.48 | 0 | 4.2 | 3.72 | 3.72 | open
122 | Kabanovo 35/10 kV | 2,5+2,5 | 0.33 | 0.22 | 120 | 0.11 | 0 | 2.625 | 2.515 | 2.515 | open | 122 | Kabanovo 35/10 kV | 2,5+2,5 | 0 | 0.33 | 0.22 | 120 | 0.11 | 0 | 2.625 | 2.515 | 2.515 | open
123 | Levkovo 35/10 kV | 1,6+1,6 | 0.22 | 0.74 | 120 | -0.52 | 0 | 1.68 | 2.2 | 2.2 | open | 123 | Levkovo 35/10 kV | 1,6+1,6 | 0.006 | 0.226 | 0.74 | 120 | -0.514 | 0 | 1.68 | 2.194 | 2.194 | open
124 | Pronino 35/10 kV | 4+2,5 | 0.38 | 0.2 | 120 | 0.18 | 0 | 2.625 | 2.445 | 2.445 | open | 124 | Pronino 35/10 kV | 4+2,5 | 0.015 | 0.395 | 0.2 | 120 | 0.195 | 0 | 2.625 | 2.43 | 2.43 | open
125 | Toltunovo 35/10 kV | 2,5+2,5 | 0.25 | 0.13 | 120 | 0.12 | 0 | 2.625 | 2.505 | 2.505 | open | 125 | Toltunovo 35/10 kV | 2,5+2,5 | 0.352 | 0.602 | 0.13 | 120 | 0.472 | 0 | 2.625 | 2.153 | 2.153 | open
126 | Soligalich 110/35/10 kV | 10+10 | 5.73 | 1.7 | 120 | 4.03 | 0 | 10.5 | 6.47 | 6.47 | open | 126 | Soligalich 110/35/10 kV | 10+10 | 0.775 | 6.505 | 1.7 | 120 | 4.805 | 0 | 10.5 | 5.695 | 5.695 | open
| Nom. Capacity MV, MVA | 10+10 | 1.15 | 0 | 120 | 1.15 | 0 | 10.5 | 9.35 |  |  |  | Nom. Capacity MV, MVA | 10+10 | 0 | 1.15 | 0 | 120 | 1.15 | 0 | 10.5 | 9.35
| Nom. Capacity LV, MVA | 10+10 | 4.58 | 1.7 | 120 | 2.88 | 0 | 10.5 | 7.62 |  |  |  | Nom. Capacity LV, MVA | 10+10 | 0.775 | 5.355 | 1.7 | 120 | 3.655 | 0 | 10.5 | 6.845
127 | Pochinok 35/10 kV | 1,6+2,5 | 0.53 | 0.34 | 120 | 0.19 | 0 | 1.68 | 1.49 | 1.49 | open | 127 | Pochinok 35/10 kV | 1,6+2,5 | 0.023 | 0.553 | 0.34 | 120 | 0.213 | 0 | 1.68 | 1.467 | 1.467 | open
128 | Chukhloma 110/35/10 kV | 6,3+6,3 | 3.97 | 2.06 | 120 | 1.91 | 0 | 6.615 | 4.705 | 4.705 | open | 128 | Chukhloma 110/35/10 kV | 6,3+6,3 | 0.598 | 4.568 | 2.06 | 120 | 2.508 | 0 | 6.615 | 4.107 | 4.107 | open
| Nom. Capacity MV, MVA | 6,3+6,3 | 1.12 | 0 | 120 | 1.12 | 0 | 6.615 | 5.495 |  |  |  | Nom. Capacity MV, MVA | 6,3+6,3 | 0 | 1.12 | 0 | 120 | 1.12 | 0 | 6.615 | 5.495
| Nom. Capacity LV, MVA | 6,3+6,3 | 2.85 | 2.06 | 120 | 0.79 | 0 | 6.615 | 5.825 |  |  |  | Nom. Capacity LV, MVA | 6,3+6,3 | 0.598 | 3.448 | 2.06 | 120 | 1.388 | 0 | 6.615 | 5.227
129 | Suday 35/10 kV | 1,6+1,6 | 1.01 | 0.49 | 120 | 0.52 | 0 | 1.68 | 1.16 | 1.16 | open | 129 | Suday 35/10 kV | 1,6+1,6 | 0.067 | 1.077 | 0.49 | 120 | 0.587 | 0 | 1.68 | 1.093 | 1.093 | open
130 | Antropovo (r) 110/35/10 kV | 6,3+16 | 6.48 | 0.38 | 120 | 6.1 | 0 | 6.615 | 0.515 | 0.515 | open | 130 | Antropovo (r) 110/35/10 kV | 6,3+16 | 0.205 | 6.685 | 0.38 | 120 | 6.305 | 0 | 6.615 | 0.31 | 0.31 | open
| Nom. Capacity MV, MVA | 6,3+16 | 4.59 | 0 | 120 | 4.59 | 0 | 6.615 | 2.025 |  |  |  | Nom. Capacity MV, MVA | 6,3+16 | 0 | 4.59 | 0 | 120 | 4.59 | 0 | 6.615 | 2.025
| Nom. Capacity LV, MVA | 6,3+16 | 1.89 | 0.38 | 120 | 1.51 | 0 | 6.615 | 5.105 |  |  |  | Nom. Capacity LV, MVA | 6,3+16 | 0.205 | 2.095 | 0.38 | 120 | 1.715 | 0 | 6.615 | 4.9
131 | Palkino 35/10 kV | 2,5+4 | 0.7 | 0.45 | 120 | 0.25 | 0 | 2.625 | 2.375 | 2.375 | open | 131 | Palkino 35/10 kV | 2,5+4 | 0.016 | 0.716 | 0.45 | 120 | 0.266 | 0 | 2.625 | 2.359 | 2.359 | open
132 | Slovinka 35/10 kV | 1,6+1,6 | 0.15 | 0.1 | 120 | 0.05 | 0 | 1.68 | 1.63 | 1.63 | open | 132 | Slovinka 35/10 kV | 1,6+1,6 | 0 | 0.15 | 0.1 | 120 | 0.05 | 0 | 1.68 | 1.63 | 1.63 | open
133 | Kady 110/35/10 kV | 10+10 | 3.87 | 0.69 | 120 | 3.18 | 0 | 10.5 | 7.32 | 7.32 | open | 133 | Kady 110/35/10 kV | 10+10 | 0.343 | 4.213 | 0.69 | 120 | 3.523 | 0 | 10.5 | 6.977 | 6.977 | open
| Nom. Capacity MV, MVA | 10+10 | 1.06 | 0 | 120 | 1.06 | 0 | 10.5 | 9.44 |  |  |  | Nom. Capacity MV, MVA | 10+10 | 0 | 1.06 | 0 | 120 | 1.06 | 0 | 10.5 | 9.44
| Nom. Capacity LV, MVA | 10+10 | 2.81 | 0.69 | 120 | 2.12 | 0 | 10.5 | 8.38 |  |  |  | Nom. Capacity LV, MVA | 10+10 | 0.343 | 3.153 | 0.69 | 120 | 2.463 | 0 | 10.5 | 8.037
134 | Ekaterinkino 35/10 kV | 1,6+1,6 | 0.09 | 0.1 | 120 | -0.01 | 0 | 1.68 | 1.69 | 1.69 | open | 134 | Ekaterinkino 35/10 kV | 1,6+1,6 | 0.05 | 0.14 | 0.1 | 120 | 0.04 | 0 | 1.68 | 1.64 | 1.64 | open
135 | Ilyinskoe 110/35/10 kV | 10+10 | 5.36 | 0.04 | 120 | 5.32 | 0 | 10.5 | 5.18 | 5.18 | open | 135 | Ilyinskoe 110/35/10 kV | 10+10 | 0 | 5.36 | 0.04 | 120 | 5.32 | 0 | 10.5 | 5.18 | 5.18 | open
| Nom. Capacity MV, MVA | 10+10 | 5.25 | 0 | 120 | 5.25 | 0 | 10.5 | 5.25 |  |  |  | Nom. Capacity MV, MVA | 10+10 | 0 | 5.25 | 0 | 120 | 5.25 | 0 | 10.5 | 5.25
| Nom. Capacity LV, MVA | 10+10 | 0.11 | 0.04 | 120 | 0.07 | 0 | 10.5 | 10.43 |  |  |  | Nom. Capacity LV, MVA | 10+10 | 0 | 0.11 | 0.04 | 120 | 0.07 | 0 | 10.5 | 10.43
136 | Kologriv 35/10 kV | 4+4 | 2.12 | 1.42 | 120 | 0.7 | 0 | 4.2 | 3.5 | 3.5 | open | 136 | Kologriv 35/10 kV | 4+4 | 0.37 | 2.49 | 1.42 | 120 | 1.07 | 0 | 4.2 | 3.13 | 3.13 | open
137 | Ovsyannikovo 35/10 kV | 1,6+1,6 | 0.4 | 0.08 | 120 | 0.32 | 0 | 1.68 | 1.36 | 1.36 | open | 137 | Ovsyannikovo 35/10 kV | 1,6+1,6 | 0 | 0.4 | 0.08 | 120 | 0.32 | 0 | 1.68 | 1.36 | 1.36 | open
138 | Makaryev-1 110/35/10 kV | 10+10 | 7.54 | 0.8 | 120 | 6.74 | 0 | 10.5 | 3.76 | 3.76 | open | 138 | Makaryev-1 110/35/10 kV | 10+10 | 0.226 | 7.766 | 0.8 | 120 | 6.966 | 0 | 10.5 | 3.534 | 3.534 | open
| Nom. Capacity MV, MVA | 10+10 | 5.36 | 0 | 120 | 5.36 | 0 | 10.5 | 5.14 |  |  |  | Nom. Capacity MV, MVA | 10+10 | 0 | 5.36 | 0 | 120 | 5.36 | 0 | 10.5 | 5.14
| Nom. Capacity MV, MVA | 10+10 | 2.18 | 0.8 | 120 | 1.38 | 0 | 10.5 | 9.12 |  |  |  | Nom. Capacity MV, MVA | 10+10 | 0.226 | 2.406 | 0.8 | 120 | 1.606 | 0 | 10.5 | 8.894
139 | Gorchukha 35/10 kV | 2,5+2,5 | 1.19 | 0 | 0 | 1.19 | 0 | 2.625 | 1.435 | 1.435 | open | 139 | Gorchukha 35/10 kV | 2,5+2,5 | 0.024 | 1.214 | 0 | 0 | 1.214 | 0 | 2.625 | 1.411 | 1.411 | open
140 | Makaryev-2 35/10 kV | 4+4 | 3 | 1.58 | 120 | 1.42 | 0 | 4.2 | 2.78 | 2.78 | open | 140 | Makaryev-2 35/10 kV | 4+4 | 0.176 | 3.176 | 1.58 | 120 | 1.596 | 0 | 4.2 | 2.604 | 2.604 | open
141 | Timoshino 35/10 kV | 1+1 | 0.18 | 0 | 0 | 0.18 | 0 | 1.05 | 0.87 | 0.87 | open | 141 | Timoshino 35/10 kV | 1+1 | 0.076 | 0.256 | 0 | 0 | 0.256 | 0 | 1.05 | 0.794 | 0.794 | open
142 | Unzha 35/10 kV | 1+1,6 | 0.81 | 0.1 | 120 | 0.71 | 0 | 1.05 | 0.34 | 0.34 | open | 142 | Unzha 35/10 kV | 1+1,6 | 0 | 0.81 | 0.1 | 120 | 0.71 | 0 | 1.05 | 0.34 | 0.34 | open
143 | Yakimovo 35/10 kV | 1,6+2,5 | 0.39 | 0.32 | 120 | 0.07 | 0 | 1.68 | 1.61 | 1.61 | open | 143 | Yakimovo 35/10 kV | 1,6+2,5 | 0 | 0.39 | 0.32 | 120 | 0.07 | 0 | 1.68 | 1.61 | 1.61 | open
144 | BKhZ 110/6 kV | 25+25 | 2.58 | 0 | 0 | 2.58 | 0 | 26.25 | 23.67 | 23.67 | open | 144 | BKhZ 110/6 kV | 25+25 | 0.225 | 2.805 | 0 | 0 | 2.805 | 0 | 26.25 | 23.445 | 23.445 | open
145 | Sosnovka 35/10 kV | 2,5+1,6 | 0.44 | 0.15 | 120 | 0.29 | 0 | 1.68 | 1.39 | 1.39 | open | 145 | Sosnovka 35/10 kV | 2,5+1,6 | 0.018 | 0.458 | 0.15 | 120 | 0.308 | 0 | 1.68 | 1.372 | 1.372 | open
146 | Georgievskoe 35/10 kV | 2,5+2,5 | 2.15 | 1.23 | 120 | 0.92 | 0 | 2.625 | 1.705 | 1.705 | open | 146 | Georgievskoe 35/10 kV | 2,5+2,5 | 0.052 | 2.202 | 1.23 | 120 | 0.972 | 0 | 2.625 | 1.653 | 1.653 | open
147 | Neya 110/35/27,5/10 kV | 40+40+6,3 | 16.05 | 3.6 | 120 | 12.45 | 0 | 48.615 | 36.165 | 36.165 | open | 147 | Neya 110/35/27,5/10 kV | 40+40+6,3 | 0.604 | 16.654 | 3.6 | 120 | 13.054 | 0 | 48.615 | 35.561 | 35.561 | open
| Nom. Capacity MV, MVA | 40+40+6,3 | 8.53 | 0 | 120 | 8.53 | 0 | 48.615 | 40.085 |  |  |  | Nom. Capacity MV, MVA | 40+40+6,3 | 0 | 8.53 | 0 | 120 | 8.53 | 0 | 48.615 | 40.085
| Nom. Capacity LV, MVA | 40+40+6,3 | 7.52 | 3.6 | 120 | 3.92 | 0 | 48.615 | 44.695 |  |  |  | Nom. Capacity LV, MVA | 40+40+6,3 | 0.604 | 8.124 | 3.6 | 120 | 4.524 | 0 | 48.615 | 44.091
148 | Vozherovo 35/10 kV | 1,6+1,6 | 0.15 | 0.12 | 120 | 0.03 | 0 | 1.68 | 1.65 | 1.65 | open | 148 | Vozherovo 35/10 kV | 1,6+1,6 | 0 | 0.15 | 0.12 | 120 | 0.03 | 0 | 1.68 | 1.65 | 1.65 | open
149 | Matveevo 35/10 kV | 1,8+4 | 0.51 | 0.42 | 120 | 0.09 | 0 | 1.89 | 1.8 | 1.8 | open | 149 | Matveevo 35/10 kV | 1,8+4 | 0.012 | 0.522 | 0.42 | 120 | 0.102 | 0 | 1.89 | 1.788 | 1.788 | open
150 | Parfenyevo 35/10 kV | 4+4 | 3.05 | 1.89 | 120 | 1.16 | 0 | 4.2 | 3.04 | 3.04 | open | 150 | Parfenyevo 35/10 kV | 4+4 | 0.07 | 3.12 | 1.89 | 120 | 1.23 | 0 | 4.2 | 2.97 | 2.97 | open
151 | Vokhma 110/35/10 kV | 6,3+16 | 5.42 | 0 | 0 | 5.42 | 0 | 6.615 | 1.195 | 1.195 | open | 151 | Vokhma 110/35/10 kV | 6,3+16 | 0.255 | 5.675 | 0 | 0 | 5.675 | 0 | 6.615 | 0.94 | 0.94 | open
| Nom. Capacity MV, MVA | 6,3+16 | 1.53 | 0 | 0 | 1.53 | 0 | 6.615 | 5.085 |  |  |  | Nom. Capacity MV, MVA | 6,3+16 | 0 | 1.53 | 0 | 0 | 1.53 | 0 | 6.615 | 5.085
| Nom. Capacity LV, MVA | 6,3+16 | 3.89 | 0 | 0 | 3.89 | 0 | 6.615 | 2.725 |  |  |  | Nom. Capacity LV, MVA | 6,3+16 | 0.255 | 4.145 | 0 | 0 | 4.145 | 0 | 6.615 | 2.47
152 | Lapshino 35/10 kV | 2,5+2,5 | 0.36 | 0.05 | 120 | 0.31 | 0 | 2.625 | 2.315 | 2.315 | open | 152 | Lapshino 35/10 kV | 2,5+2,5 | 0 | 0.36 | 0.05 | 120 | 0.31 | 0 | 2.625 | 2.315 | 2.315 | open
153 | Spass 35/10 kV | 1,6+2,5 | 0.35 | 0.35 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 | open | 153 | Spass 35/10 kV | 1,6+2,5 | 0.006 | 0.356 | 0.35 | 120 | 0.006 | 0 | 1.68 | 1.674 | 1.674 | open
154 | Bogovarovo 35/10 kV | 2,5+4 | 1.59 | 1 | 120 | 0.59 | 0 | 2.625 | 2.035 | 2.035 | open | 154 | Bogovarovo 35/10 kV | 2,5+4 | 0.061 | 1.651 | 1 | 120 | 0.651 | 0 | 2.625 | 1.974 | 1.974 | open
155 | Pavino 110/35/10 kV | 10+6,3 | 2.56 | 0 | 0 | 2.56 | 0 | 6.615 | 4.055 | 4.055 | open | 155 | Pavino 110/35/10 kV | 10+6,3 | 0.068 | 2.628 | 0 | 0 | 2.628 | 0 | 6.615 | 3.987 | 3.987 | open
| Nom. Capacity MV, MVA | 10+6,3 | 0.44 | 0 | 0 | 0.44 | 0 | 6.615 | 6.175 |  |  |  | Nom. Capacity MV, MVA | 10+6,3 | 0 | 0.44 | 0 | 0 | 0.44 | 0 | 6.615 | 6.175
| Nom. Capacity LV, MVA | 10+6,3 | 2.12 | 0 | 0 | 2.12 | 0 | 6.615 | 4.495 |  |  |  | Nom. Capacity LV, MVA | 10+6,3 | 0.068 | 2.188 | 0 | 0 | 2.188 | 0 | 6.615 | 4.427
156 | Ledengskaya 35/10 kV | 1,6+4 | 0.08 | 0.07 | 120 | 0.01 | 0 | 1.68 | 1.67 | 1.67 | open | 156 | Ledengskaya 35/10 kV | 1,6+4 | 0 | 0.08 | 0.07 | 120 | 0.01 | 0 | 1.68 | 1.67 | 1.67 | open
157 | Pyshchug 110/35/10 kV | 6,3+6,3 | 2.42 | 0 | 0 | 2.42 | 0 | 6.615 | 4.195 | 4.195 | open | 157 | Pyshchug 110/35/10 kV | 6,3+6,3 | 1.586 | 4.006 | 0 | 0 | 4.006 | 0 | 6.615 | 2.609 | 2.609 | open
| Nom. Capacity MV, MVA | 6,3+6,3 | 0.12 | 0 | 0 | 0.12 | 0 | 6.615 | 6.495 |  |  |  | Nom. Capacity MV, MVA | 6,3+6,3 | 0 | 0.12 | 0 | 0 | 0.12 | 0 | 6.615 | 6.495
| Nom. Capacity LV, MVA | 6,3+6,3 | 2.3 | 0 | 0 | 2.3 | 0 | 6.615 | 4.315 |  |  |  | Nom. Capacity LV, MVA | 6,3+6,3 | 1.586 | 3.886 | 0 | 0 | 3.886 | 0 | 6.615 | 2.729
158 | Rozhdestvenskoe 110/35/10 kV | 10+4 | 1.77 | 0.75 | 120 | 1.02 | 0 | 4.2 | 3.18 | 3.18 | open | 158 | Rozhdestvenskoe 110/35/10 kV | 10+4 | 0.139 | 1.909 | 0.75 | 120 | 1.159 | 0 | 4.2 | 3.041 | 3.041 | open
| Nom. Capacity MV, MVA | 10+4 | 0.69 | 0 | 120 | 0.69 | 0 | 4.2 | 3.51 |  |  |  | Nom. Capacity MV, MVA | 10+4 | 0 | 0.69 | 0 | 120 | 0.69 | 0 | 4.2 | 3.51
| Nom. Capacity LV, MVA | 10+4 | 1.08 | 0.75 | 120 | 0.33 | 0 | 4.2 | 3.87 |  |  |  | Nom. Capacity LV, MVA | 10+4 | 0.139 | 1.219 | 0.75 | 120 | 0.469 | 0 | 4.2 | 3.731
159 | Odoevskoe 35/10 kV | 1,6+1,6 | 0.37 | 0.27 | 120 | 0.1 | 0 | 1.68 | 1.58 | 1.58 | open | 159 | Odoevskoe 35/10 kV | 1,6+1,6 | 0.024 | 0.394 | 0.27 | 120 | 0.124 | 0 | 1.68 | 1.556 | 1.556 | open
160 | Sharya (r) 110/35/6 kV | 20+25 | 19.02 | 2 | 120 | 17.02 | 0 | 21 | 3.98 | 3.98 | open | 160 | Sharya (r) 110/35/6 kV | 20+25 | 0.349 | 19.369 | 2 | 120 | 17.369 | 0 | 21 | 3.631 | 3.631 | open
| Nom. Capacity MV, MVA | 20+25 | 12.2 | 0 | 120 | 12.2 | 0 | 21 | 8.8 |  |  |  | Nom. Capacity MV, MVA | 20+25 | 0 | 12.2 | 0 | 120 | 12.2 | 0 | 21 | 8.8
| Nom. Capacity LV, MVA | 20+25 | 6.82 | 2 | 120 | 4.82 | 0 | 21 | 16.18 |  |  |  | Nom. Capacity LV, MVA | 20+25 | 0.349 | 7.169 | 2 | 120 | 5.169 | 0 | 21 | 15.831
161 | Industrial hub 110/6/6 kV | 25+25 | 5.71 | 2.5 | 120 | 3.21 | 0 | 26.25 | 23.04 | 23.04 | open | 161 | Industrial hub 110/6/6 kV | 25+25 | 0.303 | 6.013 | 2.5 | 120 | 3.513 | 0 | 26.25 | 22.737 | 22.737 | open
162 | Krivyachka 35/10 kV | 1,6+1 | 0.82 | 0.57 | 120 | 0.25 | 0 | 1.05 | 0.8 | 0.8 | open | 162 | Krivyachka 35/10 kV | 1,6+1 | 0.01 | 0.83 | 0.57 | 120 | 0.26 | 0 | 1.05 | 0.79 | 0.79 | open
163 | Nikolo-Shanga 35/10 kV | 1,6+1,6 | 0.89 | 0 | 0 | 0.89 | 0 | 1.68 | 0.79 | 0.79 | open | 163 | Nikolo-Shanga 35/10 kV | 1,6+1,6 | 0.184 | 1.074 | 0 | 0 | 1.074 | 0 | 1.68 | 0.606 | 0.606 | open
164 | Tsentralnaya 35/6 kV | 10+10 | 8.96 | 3 | 120 | 5.96 | 0 | 10.5 | 4.54 | 4.54 | open | 164 | Tsentralnaya 35/6 kV | 10+10 | 1.797 | 10.757 | 3 | 120 | 7.757 | 0 | 10.5 | 2.743 | 2.743 | open
| Total over Kostromaenergo | 1705 | 423.835 | [8 empty] | 2: Total over Kostromaenergo; 3: 1705; 5: 525.082
| deficit | [8 empty] | -6.235 |  | 2: deficit; Min 12: -13.076
| proficit | [8 empty] | 502.7 |  | 2: proficit; Min 12: 412.914

## Свод.тек. дефицит март 2011
The list of closed supply centers of IDGC of Centre - Kostromaenergo division (current deficit of capacity).
No. | Name of supply center, voltage class |  | Current deficit, MVA
Kostromaenergo
1 | Kostroma-3 110/35/10 kV | 10+16 | -0.99
2 | Vostochnaya-1 35/6 kV | 10+10+6,3 | -5.245
Total current deficit (2011) |  |  | -6.235

## Свод. ож. дефицит март 2011
The list of closed supply centers of IDGC of Centre - Kostromaenergo division with expected load taking into account new connections and other development of the electical networks (expected deficit of capacity).
No. | Name of supply center, voltage class |  | Expected deficit, MVA
Kostromaenergo
1 | Sandogora 35/6 kV | 1 | -0.003
2 | Priskokovo 35/10kV | 2.5 | -0.166
3 | Sukhonogovo 35/10 kV | 3,2+4 | -0.372
4 | Kostroma-3 110/35/10 kV | 10+16 | -2.977
5 | Kostroma-1 110/6 kV | 10+10 | -0.996
6 | Severnaya 110/6 kV | 20+25 | -0.458
7 | Vostochnaya-1 35/6 kV | 10+10+6,3 | -7.757
8 | KPD 110/35/10 kV | 16+16 | -0.347
Total expected deficit (March 2011) |  |  | -13.076