## МРСК
Calculation of transmission capacity of Main substations of the branch "Belgorodenergo" of IDGC of Centre, JSC following the results of winter measurement of peak load of 2009. | [14 empty] | 1000
Table 1
No. | Object of main substation, voltage class | Current deficit | [10 empty] | Note
|  | Installed power capacity of transformers Sуst. Including their number, pcs/ MVA | P | Q | Summary total capacity of central substation following the results of measurements of load maximal Sмах | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit/proficit of Main Substation, MVA
[5 empty] | MVA | MVA | Min
1 | 2 | 4 |  |  | 5 | 6 | 7 | 8 | 9 | 10 | 11 |  | 12
One-transformer substations
1 | SS-110/35/10kv D.Polyana | 6.3 | 1523 | 679 | 1.6675 | 1.457 | 45 | 1.457 | 0 | 1.457 | -0.2105 | -0.57942 |  |  | D.Polyana | 1.4535
| Sн. MV, МVА | 6.3 | 513 | 301 | 0.59479 | 0.958 |  | 0.958 | 0 | 0.958 | 0.36321 |  |  |  | Konshino | 0.38327
| Sн. LV, МVА | 6.3 | 1010 | 378 | 1.0784 | 0.499 |  | 0.499 | 0 | 0.499 | -0.57942 |  |  |  | Orositelnaya | 11.6065
2 | SS-110/35/10kv Konshino | 6.3 | 375 | 154 | 0.40539 | 0.39 | 20 | 0.39 | 0 | 0.39 | -0.01539 | -0.01539 |  |  | Pishcheprom | 6.4309
| Sн. MV, МVА | 6.3 |  |  | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | Rovenki-110 | 2.2902
| Sн. LV, МVА | 6.3 | 375 | 154 | 0.40539 | 0.39 |  | 0.39 | 0 | 0.39 | -0.01539 |  |  |  | Serebryanka | 1.2339
3 | SS-110/35/10kv Orositelnaya | 16 | 11884 | 2898 | 12.2322 | 11.607 | 120 | 11.607 | 0 | 11.607 | -0.62525 | -0.90525
| Sн. MV, МVА | 16 | 9059 | 2898 | 9.5113 | 8.606 |  | 8.606 | 0 | 8.606 | -0.90525
| Sн. LV, МVА | 16 | 2825 |  | 2.825 | 3.001 |  | 3.001 | 0 | 3.001 | 0.176
4 | SS-110/35/6kv Pishcheprom | 25 | 6036 | 1850 | 6.3131 | 6.679 | 120 | 6.679 | 0 | 6.679 | 0.36586 | -0.24769
| Sн. MV, МVА | 12.5 | 2171 | 662 | 2.2697 | 2.022 |  | 2.022 | 0 | 2.022 | -0.24769
| Sн. LV, МVА | 12.5 | 3865 | 1188 | 4.0435 | 4.657 |  | 4.657 | 0 | 4.657 | 0.61354
5 | SS-110/35/10kv Rovenki | 16 | 2453 | 976 | 2.64 | 3.44 | 120 | 3.44 | 0 | 3.44 | 0.79996 | 0.79996
| Sн. MV, МVА | 16 | 2 | 34 | 0.034059 | 4 |  | 4 | 0 | 4 | 3.9659
| Sн. LV, МVА | 16 | 2451 | 942 | 2.6258 | 3.44 |  | 3.44 | 0 | 3.44 | 0.81421
6 | SS-110/35/10kv Serebryanka | 10 | 1181 | 534 | 1.2961 | 1.78 | 45 | 1.78 | 0 | 1.78 | 0.48388 | 0
| Sн. MV, МVА | 10 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
| Sн. LV, MVА | 10 | 1181 | 534 | 1.2961 | 1.78 |  | 1.78 | 0 | 1.78 | 0.48388
7 | SS-35/10kv Afanasyevka | 1.6 | 868 | 280 | 0.91204 | 0.6464 | 45 | 0.6464 | 0 | 0.6464 | -0.26564 | -0.26564
8 | SS-35/10kv Borisovka | 1.6 | 576 | 192 | 0.60716 | 0.6835 | 45 | 0.6835 | 0 | 0.6835 | 0.076343 | 0.076343
9 | SS-35/10kv Borisy | 1.6 | 432 | 234 | 0.4913 | 0 | 20 | 0 | 0 | 0 | -0.4913 | -0.4913
10 | SS-35/10kv Gostishchevo | 4 | 3792 | 1440 | 4.0562 | 2.64 | 80 | 2.64 | 0 | 2.64 | -1.4162 | -1.4162
11 | SS-35/10kv Gruzskoe | 1.6 | 606 | 264 | 0.66101 | 1.05 | 80 | 1.05 | 0 | 1.05 | 0.38899 | 0.38899
12 | SS-35/10kv Zemsnaryad | 1.6 | 14 | 14 | 0.019799 | 0 |  | 0 | 0 | 0 | -0.019799 | -0.019799
13 | SS-35/10kv Kazachya Lisitsa | 2.5 | 360 | 112 | 0.37702 | 0 |  | 0 | 0 | 0 | -0.37702 | -0.37702
14 | SS-35/10kv Kamyzino | 2.5 | 992 | 392 | 1.0666 | 0.541 | 45 | 0.541 | 0 | 0.541 | -0.52564 | -0.52564
15 | SS-35/10kv Koloskovo | 2.5 | 2000 | 624 | 2.0951 | 1.6626 | 45 | 1.6626 | 0 | 1.6626 | -0.43248 | -0.43248
16 | SS-35/10jkv Kryukovo | 2.5 | 1584 | 492 | 1.6587 | 1.55 | 45 | 1.55 | 0 | 1.55 | -0.10865 | -0.10865
17 | SS-35/10kv Kushchino | 1.6 | 384 | 144 | 0.41011 | 0.4101 | 80 | 0.4101 | 0 | 0.4101 | -1.218e-05 | -1.218e-05
18 | SS-35/10kv Lopukhinka | 2.5 | 384 | 160 | 0.416 | 0.407 | 20 | 0.407 | 0 | 0.407 | -0.009 | -0.009
19 | SS-35/10kv Malakeevo | 2.5 | 1296 | 648 | 1.449 | 1.38 | 120 | 1.38 | 0 | 1.38 | -0.068972 | -0.068972
20 | SS-35/10kv Murom | 2.5 | 1336 | 432 | 1.4041 | 1.54 | 45 | 1.54 | 0 | 1.54 | 0.13589 | 0.13589
21 | SS-35/10kv Nikolaevka | 2.5 | 664 | 288 | 0.72377 | 0.6647 | 45 | 0.6647 | 0 | 0.6647 | -0.059068 | -0.059068
22 | SS-35/10kv Nikolskoe | 4 | 1776 | 396 | 1.8196 | 0.78 | 120 | 0.78 | 0 | 0.78 | -1.0396 | -1.0396
23 | SS-35/10kv Pokrovka | 4 | 708 | 300 | 0.76894 | 0.722 | 45 | 0.722 | 0 | 0.722 | -0.046937 | -0.046937
24 | SS-35/10kv Pyatnitskoe | 4 | 2441 | 768 | 2.559 | 1.84 | 80 | 1.84 | 0 | 1.84 | -0.71897 | -0.71897
25 | SS-35/10kv Sugar plant Ivnya | 2.5 | 94 | 151 | 0.17787 | 1.676 | 80 | 1.676 | 0 | 1.676 | 1.4981 | 1.4981
26 | SS-35/10kv Svistovka | 2.5 | 616 | 304 | 0.68693 | 0.6872 | 45 | 0.6872 | 0 | 0.6872 | 0.0002706 | 0.0002706
27 | SS-35/10kv sovkhoz "Urazovsky" | 2.5 | 688 | 244 | 0.72999 | 0.7238 | 120 | 0.7238 | 0 | 0.7238 | -0.0061863 | -0.0061863
28 | SS-35/10kv Kharkovskaya | 2.5 | 660 | 304 | 0.72665 | 0.6797 | 120 | 0.6797 | 0 | 0.6797 | -0.046947 | -0.046947
29 | SS-35/10kv Tserkovnaya | 2.5 | 1112 | 288 | 1.1487 | 1 | 80 | 1 | 0 | 1 | -0.14869 | -0.14869
Two- and more transformer substations
30 | SS-110/6kv Automobile maintenance plant | 16+16 | 13361 | 7836 | 15.4893 | 3.561 | 45 | 11.9283 | 0 | 16.8 | 4.8717 | 4.8717 |  | 1.05 | 16 |  | Automobile maintenance plant | 9.9792
31 | SS-110/35/10kv Aydar | 16+10 | 9152 | 3513 | 9.8031 | 8.95 | 120 | 0.85307 | 0 | 10.5 | 9.6469 | 9.6416 |  | 1.05 | 10 |  | Aydar | 8.4408
| Sн. MV, МVА | 16+10 | 7582 | 2985 | 8.1484 | 7.29 |  | 0.85843 | 0 | 10.5 | 9.6416 |  |  | 1.05 | 10 |  | Alexandrovka | 12.534
| Sн. LV, МVА | 16+10 | 1570 | 528 | 1.6564 | 1.66 |  | -0.003593 | 0 | 10.5 | 10.5036 |  |  | 1.05 | 10 |  | Alexeevka | 44.0632
32 | SS-110/35/10kv Alexandrovka | 16+16 | 12411 | 4290 | 13.1315 | 8.37 | 80 | 4.7615 | 0 | 16.8 | 12.0385 | 12.0385 |  | 1.05 | 16 |  | Arkhangelskoe | 9.383
| Sн. MV, МVА | 16+16 | 6573 | 2264 | 6.952 | 6.697 |  | 0.25498 | 0 | 16.8 | 16.545 |  |  | 1.05 | 16 |  | Belgorod-1 | 44.5181
| Sн. LV, МVА | 16+16 | 5838 | 2026 | 6.1796 | 1.673 |  | 4.5066 | 0 | 16.8 | 12.2934 |  |  | 1.05 | 16 |  | Borisovka | 14.4143
33 | SS-110/35/10kv Alexeevka | 25+25+25 | 39765 | 17571 | 43.4741 | 5.322 | 120 | 38.1521 | 0 | 52.5 | 14.3479 | 14.3479 |  | 1.05 | 50 |  | V.Pokrovka | 9.036
| Sн. MV, МVА | 25+25+25 | 16965 | 8691 | 19.0616 | 3.102 |  | 15.9596 | 0 | 52.5 | 36.5404 |  |  | 1.05 | 50 |  | Veydelevka | 7.9503
| Sн. LV, МVА | 25+25+25 | 22800 | 8880 | 24.4682 | 2.22 |  | 22.2482 | 0 | 52.5 | 30.2518 |  |  | 1.05 | 50 |  | Vitamin plant | 11.7863
34 | SS-110/35/10kv Arkhangelskoe | 10+16 | 10006 | 3960 | 10.7611 | 8.87 | 45 | 1.8911 | 0 | 10.5 | 8.6089 | 8.6089 |  | 1.05 | 10 |  | Volokonovka | 15.9084
| Sн. MV, МVА | 10+16 | 9416 | 3776 | 10.1449 | 8.867 |  | 1.2779 | 0 | 10.5 | 9.2221 |  |  | 1.05 | 10 |  | Vostochnaya | 41.987
| Sн. LV, МVА | 10+16 | 590 | 184 | 0.61803 | 0 |  | 0.61803 | 0 | 10.5 | 9.882 |  |  | 1.05 | 10 |  | Golofeevka | 1.8481
35 | SS-110/6kv Belgorod-1 | 40+48 | 42786 | 13076 | 44.7395 | 0 | 120 | 44.7395 | 0 | 42 | -2.7395 | -2.7395 |  | 1.05 | 40 |  | Gotnya | 8.9986
36 | SS-110/35/10kv Borisovka | 16+16 | 11354 | 4570 | 12.2392 | 11.433 | 120 | 0.80621 | 0 | 16.8 | 15.9938 | 4.8462 |  | 1.05 | 16 |  | Grayvoron | 15.2094
| Sн. MV, МVА | 16+8 | 4826 | 2482 | 5.4268 | 8.133 |  | -2.7062 | 0 | 8.4 | 11.1062 |  |  | 1.05 | 8 |  | Donets | 26.0404
| Sн. LV, МVА | 16+8 | 6528 | 2088 | 6.8538 | 3.3 |  | 3.5538 | 0 | 8.4 | 4.8462 |  |  | 1.05 | 8 |  | Dubovoe | 22.9597
37 | SS-110/35/10kv V.Pokrovka | 10+10 | 9651 | 3834 | 10.3847 | 11.5 | 120 | -1.1153 | 0 | 10.5 | 11.6153 | 9.4887 |  | 1.05 | 10 |  | Zhuravliki | 13.1662
| Sн. MV, МVА | 10+10 | 8148 | 3354 | 8.8113 | 7.8 |  | 1.0113 | 0 | 10.5 | 9.4887 |  |  | 1.05 | 10 |  | Zapadnaya | 16.9475
| Sн. LV, МVА | 10+10 | 1503 | 480 | 1.5778 | 3.7 |  | -2.1222 | 0 | 10.5 | 12.6222 |  |  | 1.05 | 10 |  | Ivnya | 6.018
38 | SS-110/35/10kv Veydelevka | 10+10 | 9151 | 3160 | 9.6812 | 8.83 | 120 | 0.85124 | 0 | 10.5 | 9.6488 | 9.1219 |  | 1.05 | 10
| Sн. MV, МVА | 10+10 | 4999 | 1858 | 5.3331 | 3.955 |  | 1.3781 | 0 | 10.5 | 9.1219 |  |  | 1.05 | 10
| Sн. LV, МVА | 10+10 | 4152 | 1302 | 4.3514 | 4.875 |  | -0.52364 | 0 | 10.5 | 11.0236 |  |  | 1.05 | 10
39 | SS-110/6kv Vitamin plant | 25+25 | 13429 | 6832 | 15.067 | 1.46 | 45 | 13.607 | 0 | 26.25 | 12.643 | 12.643 |  | 1.05 | 25
40 | SS-110/35/10kv Volokonovka | 25+25 | 18812 | 6807 | 20.0057 | 10.651 | 120 | 9.3547 | 0 | 26.25 | 16.8953 | 16.8953 |  | 1.05 | 25
| Sн. MV, МVА | 25+25 | 10517 | 4038 | 11.2656 | 8.576 |  | 2.6896 | 0 | 26.25 | 23.5604 |  |  | 1.05 | 25
| Sн. LV, МVА | 25+25 | 8295 | 2769 | 8.745 | 2.075 |  | 6.67 | 0 | 26.25 | 19.58 |  |  | 1.05 | 25
41 | SS-110/35/6kv Vostochnaya | 25+25 | 37165 | 16321 | 40.5908 | 25.07 | 120 | 15.5208 | 0 | 26.25 | 10.7292 | 6.2914 |  | 1.05 | 25
| Sн. MV, МVА | 25+25 | 16029 | 5536 | 16.9581 | 21.3 |  | -4.3419 | 0 | 26.25 | 30.5919 |  |  | 1.05 | 25
| Sн. LV, МVА | 25+25 | 21136 | 10785 | 23.7286 | 3.77 |  | 19.9586 | 0 | 26.25 | 6.2914 |  |  | 1.05 | 25
42 | SS-110/10/6kv Golofeevka | 25+25 | 2404 | 964 | 2.5901 | 0 |  | 2.5901 | 0 | 26.25 | 23.6599 | 10.5349 |  | 1.05 | 25
| Sн. MV, МVА | 12,5+12,5 | 0 | 0 | 0 | 0 |  | 0 | 0 | 13.125 | 13.125 |  |  | 1.05 | 12.5
| Sн. LV, МVА | 12,5+12,5 | 2404 | 964 | 2.5901 | 0 |  | 2.5901 | 0 | 13.125 | 10.5349 |  |  | 1.05 | 12.5
43 | SS-110/10kv Gotnya | 16+16 | 8388 | 3608 | 9.1311 | 6.43 | 120 | 2.7011 | 0 | 16.8 | 14.0989 | 14.0989 |  | 1.05 | 16
44 | SS-110/35/10kv Grayvoron | 16+16 | 13281 | 5063 | 14.2133 | 13.953 | 80 | 0.26034 | 0 | 16.8 | 16.5397 | 14.4501 |  | 1.05 | 16
| Sн. MV, МVА | 16+16 | 8161 | 3347 | 8.8207 | 10.903 |  | -2.0823 | 0 | 16.8 | 18.8823 |  |  | 1.05 | 16
| Sн. LV, МVА | 16+16 | 5120 | 1716 | 5.3999 | 3.05 |  | 2.3499 | 0 | 16.8 | 14.4501 |  |  | 1.05 | 16 |  | K.Gvardiya | 11.3866
45 | SS-110/6kv Donets | 40+40 | 26016 | 7584 | 27.0989 | 6.73 | 120 | 20.3689 | 0 | 42 | 21.6311 | 21.6311 |  | 1.05 | 40 |  | Kazatskie Bugry | 11.6977
46 | SS-110/10kv Dubovoe | 40+40 | 23785 | 4642 | 24.2337 | 11.23 | 120 | 13.0037 | 0 | 42 | 28.9963 | 28.9963 |  | 1.05 | 40 |  | Korocha | 18.4946
47 | SS-110/35/6kv Zhuravliki | 40+25 | 23335 | 7691 | 24.5698 | 12.4 | 120 | 12.1698 | 0 | 42 | 29.8302 | 29.8302 |  | 1.05 | 40 |  | Krasnaya Yaruga | 10.8277
| Sн. MV, МVА | 40+25 | 16567 | 6202 | 17.6898 | 6.227 |  | 11.4628 | 0 | 42 | 30.5372 |  |  | 1.05 | 40 |  | Maximovka | 10.7359
| Sн. LV, МVА | 40+25 | 6768 | 1489 | 6.9299 | 6.173 |  | 0.75686 | 0 | 42 | 41.2431 |  |  | 1.05 | 40 |  | N.Oskol | 19.8083
48 | SS-110/10kv Zapadnaya | 16+16 | 15459 | 3295 | 15.8063 | 1.249 | 80 | 14.5573 | 0 | 16.8 | 2.2427 | 2.2427 |  | 1.05 | 16
49 | SS-110/35/10kv Ivnya | 10+10 | 5960 | 2270 | 6.3777 | 6.16 | 80 | 0.21766 | 0 | 10.5 | 10.2823 | 10.2823 |  | 1.05 | 10
| Sн. MV, МVА | 10+10 | 2266 | 1008 | 2.4801 | 2.375 |  | 0.10508 | 0 | 10.5 | 10.3949 |  |  | 1.05 | 10
| Sн. LV, МVА | 10+10 | 3694 | 1262 | 3.9036 | 3.785 |  | 0.11862 | 0 | 10.5 | 10.3814 |  |  | 1.05 | 10
50 | SS-110/35/10kv K.Gvardiya | 16+16 | 16357 | 6666 | 17.6632 | 7.7116 | 120 | 9.9516 | 0 | 16.8 | 6.8484 | 6.8484 |  | 1.05 | 16
| Sн. MV, МVА | 16+16 | 8971 | 4110 | 9.8677 | 4.854 |  | 5.0137 | 0 | 16.8 | 11.7863 |  |  | 1.05 | 16
| Sн. LV, МVА | 16+16 | 7386 | 2556 | 7.8158 | 2.8576 |  | 4.9582 | 0 | 16.8 | 11.8418 |  |  | 1.05 | 16
51 | SS-110/10/6kv Kazatskie Bugry | 25+25 | 12571 | 3927 | 13.1701 | 9.65 | 80 | 3.5201 | 0 | 26.25 | 22.7299 | 18.8414 |  | 1.05 | 25
| Sн. MV, МVА | 25+25 | 1720 | 404 | 1.7668 | 1.384 |  | 0.38281 | 0 | 26.25 | 25.8672 |  |  | 1.05 | 25
| Sн. LV, МVА | 25+25 | 10851 | 3523 | 11.4086 | 4 |  | 7.4086 | 0 | 26.25 | 18.8414 |  |  | 1.05 | 25
52 | SS-110/35/10kv Korocha | 16+16+16 | 20632 | 7838 | 22.0707 | 2.019 | 20 | 20.0517 | 0 | 33.6 | 13.5483 | 13.5483 |  | 1.05 | 32
| Sн. MV, МVА | 16+16+16 | 8114 | 2802 | 8.5842 | 1.719 |  | 6.8652 | 0 | 33.6 | 26.7348 |  |  | 1.05 | 32
| Sн. LV, МVА | 16+16+16 | 12518 | 5036 | 13.493 | 0.3 |  | 13.193 | 0 | 33.6 | 20.407 |  |  | 1.05 | 32
53 | SS-110/10kv Krapivenskaya | 16+16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.8 | 16.8 | 16.8 |  | 1.05 | 16
54 | SS-110/35/10kv Krasnaya Yaruga | 10+10 | 9903 | 3556 | 10.5221 | 9.158 | 120 | 1.3641 | 0 | 10.5 | 9.1359 | 9.1359 |  | 1.05 | 10
| Sн. MV, МVА | 10+10 | 4393 | 1542 | 4.6558 | 3.52 |  | 1.1358 | 0 | 10.5 | 9.3642 |  |  | 1.05 | 10
| Sн. LV, МVА | 10+10 | 5510 | 2014 | 5.8665 | 5.638 |  | 0.22854 | 0 | 10.5 | 10.2715 |  |  | 1.05 | 10
55 | SS-110/10/10kv Mayskaya | 40+40 | 2581 | 670 | 2.6665 |  |  | 2.6665 | 0 | 42 | 39.3335 | 39.3335 |  | 1.05 | 40
56 | SS-110/35/10kv Maximovka | 16+16 | 7328 | 4264 | 8.4783 | 11.48 | 45 | -3.0017 | 0 | 16.8 | 19.8017 | 17.792 |  | 1.05 | 16
| Sн. MV, МVА | 16+16 | 6384 | 3830 | 7.4448 | 9.449 |  | -2.0042 | 0 | 16.8 | 18.8042 |  |  | 1.05 | 16
| Sн. LV, МVА | 16+16 | 944 | 434 | 1.039 | 2.031 |  | -0.99201 | 0 | 16.8 | 17.792 |  |  | 1.05 | 16
57 | SS-110/35/10kv N.Oskol | 25+31,5 | 21159 | 8583 | 22.8336 | 9.119 | 80 | 13.7146 | 0 | 26.25 | 12.5354 | 12.5354 |  | 1.05 | 25
| Sн. MV, МVА | 25+31,5 | 7395 | 3599 | 8.2243 | 7.83 |  | 0.39428 | 0 | 26.25 | 25.8557 |  |  | 1.05 | 25 |  | Obukhovskaya | 2.351
| Sн. LV, МVА | 25+31,5 | 13764 | 4984 | 14.6386 | 1.289 |  | 13.3496 | 0 | 26.25 | 12.9004 |  |  | 1.05 | 25 |  | Ochistnye | 6.5595
58 | SS-110/10kv Obukhovskaya | 25+25 | 2272 | 372 | 2.3023 | 0 |  | 2.3023 | 0 | 26.25 | 23.9477 | 23.9477 |  | 1.05 | 25 |  | Promyshlennaya | 14.983
59 | SS-110/6kv Ochistnye | 16+16 | 5231 | 2499 | 5.7973 | 0 |  | 5.7973 | 0 | 16.8 | 11.0027 | 11.0027 |  | 1.05 | 16 |  | Poultry plant | 10.559
60 | SS-110/10kv Promyshlennaya | 25+25 | 15509 | 7413 | 17.1896 | 0 |  | 17.1896 | 0 | 26.25 | 9.0604 | 9.0604 |  | 1.05 | 25 |  | Pushkarnaya | 27.735
61 | SS-110/10kv Poultry plant | 16+16 | 9980 | 5649 | 11.4679 | 1.296 | 80 | 10.1719 | 0 | 16.8 | 6.6281 | 6.6281 |  | 1.05 | 16 |  | Rakitnoe | 9.2018
62 | SS-110/10kv Pushkarnaya | 40+40 | 33540 | 9360 | 34.8216 | 0 | 60 | 34.8216 | 0 | 42 | 7.1784 | 7.1784 |  | 1.05 | 40 |  | Rudnik | 14.117
63 | SS-110/35/10kv Rakitnoe | 10+10 | 10160 | 3946 | 10.8994 | 8.98 | 120 | 1.9194 | 0 | 10.5 | 8.5806 | 7.7972 |  | 1.05 | 10 |  | Severnaya | 11.1616
| Sн. MV, МVА | 10+10 | 4944 | 3154 | 5.8644 | 6.407 |  | -0.54263 | 0 | 10.5 | 11.0426 |  |  | 1.05 | 10 |  | Skorodnoe | 11.5224
| Sн. LV, МVА | 10+10 | 5216 | 792 | 5.2758 | 2.573 |  | 2.7028 | 0 | 10.5 | 7.7972 |  |  | 1.05 | 10 |  | St.Oskol - 1 | 28.8772
64 | SS-110/35/6kv Rudnik | 25+25 | 16284 | 8685 | 18.4553 | 10.46 | 45 | 7.9953 | 0 | 26.25 | 18.2547 | 18.2547 |  | 1.05 | 25 |  | Streletskaya | 4.2243
| Sн. MV, МVА | 25+25 | 10147 | 5511 | 11.547 | 10.46 |  | 1.087 | 0 | 26.25 | 25.163 |  |  | 1.05 | 25 |  | Stroitel | 13.298
| Sн. LV, МVА | 25+25 | 6137 | 3174 | 6.9092 | 0 |  | 6.9092 | 0 | 26.25 | 19.3408 |  |  | 1.05 | 25 |  | Tomarovka | 12.5522
65 | SS-110/10kv Severnaya | 40+40 | 12059 | 3183 | 12.472 | 3.312 | 45 | 9.16 | 0 | 42 | 32.84 | 32.84 |  | 1.05 | 40 |  | Chemical plant | 10.0162
66 | SS-110/35/10kv Skorodnoe | 16+16 | 11370 | 3385 | 11.8632 | 10.36 | 120 | 1.5032 | 0 | 16.8 | 15.2968 | 15.2968 |  | 1.05 | 16 |  | Tsentralnaya | 22.8863
| Sн. MV, МVА | 16+16 | 7443 | 2214 | 7.7653 | 7.562 |  | 0.20331 | 0 | 16.8 | 16.5967 |  |  | 1.05 | 16 |  | Cheremoshnoe | 23.7143
| Sн. LV, МVА | 16+16 | 3927 | 1171 | 4.0979 | 2.798 |  | 1.2999 | 0 | 16.8 | 15.5001 |  |  | 1.05 | 16 |  | Chernyanka | 14.7605
67 | SS-110/35/6kv St.Oskol - 1 | 20+25+25 | 27161 | 10201 | 29.0135 | 0 |  | 29.0135 | 0 | 47.25 | 18.2365 | 18.2365 |  | 1.05 | 45 |  | Shebekino | 25.5429
| Sн. MV, МVА | 20+25+25 | 5305 | 2289 | 5.7778 | 0 |  | 5.7778 | 0 | 47.25 | 41.4722 |  |  | 1.05 | 45 |  | Sheino | 2.4086
| Sн. LV, МVА | 20+25+25 | 21856 | 7912 | 23.244 | 0 |  | 23.244 | 0 | 47.25 | 24.006 |  |  | 1.05 | 45 |  | Yuzhnaya | 43.0909
68 | SS-110/35/10kv Streletskaya | 16+16 | 6052 | 1769 | 6.3052 | 2.23 | 80 | 4.0752 | 0 | 16.8 | 12.7248 | 4.3575 |  | 1.05 | 16
| Sн. MV, МVА | 16+8 | 7 | 95 | 0.095258 | 0 |  | 0.095258 | 0 | 8.4 | 8.3047 |  |  | 1.05 | 8
| Sн. LV, МVА | 16+8 | 6045 | 1674 | 6.2725 | 2.23 |  | 4.0425 | 0 | 8.4 | 4.3575 |  |  | 1.05 | 8
69 | SS-110/6kv Stroitel | 15+15 | 14665 | 5743 | 15.7494 | 0 |  | 15.7494 | 0 | 15.75 | 0.00057861 | 0.00057861 |  | 1.05 | 15
70 | SS-110/35/10kv Tomarovka | 16+16 | 12522 | 4336 | 13.2515 | 3.46 | 45 | 9.7915 | 0 | 16.8 | 7.0085 | 7.0085 |  | 1.05 | 16
| Sн. MV, МVА | 16+16 | 4590 | 1614 | 4.8655 | 3.46 |  | 1.4055 | 0 | 16.8 | 15.3945 |  |  | 1.05 | 16
| Sн. LV, МVА | 16+16 | 7932 | 2722 | 8.3861 | 0 |  | 8.3861 | 0 | 16.8 | 8.4139 |  |  | 1.05 | 16
71 | SS-110/6kv Chemical plant | 32+32 | 8580 | 3308 | 9.1956 | 5.56 | 45 | 3.6356 | 0 | 33.6 | 29.9644 | 29.9644 |  | 1.05 | 32
72 | SS-110/10kv Tsentralnaya | 40+40 | 31170 | 5706 | 31.688 | 0 |  | 31.688 | 0 | 42 | 10.312 | 10.312 |  | 1.05 | 40
73 | SS-110/35/10kv Cheremoshnoe | 25+25 | 23134 | 8712 | 24.7201 | 20.54 | 80 | 4.1801 | 0 | 26.25 | 22.0699 | 22.0699 |  | 1.05 | 25
| Sн. MV, МVА | 25+25 | 21521 | 7872 | 22.9155 | 19.676 |  | 3.2395 | 0 | 26.25 | 23.0105 |  |  | 1.05 | 25
| Sн. LV, МVА | 25+25 | 1613 | 840 | 1.8186 | 0 |  | 1.8186 | 0 | 26.25 | 24.4314 |  |  | 1.05 | 25
74 | SS-110/35/10kv Chernyanka | 16+16 | 16319 | 6059 | 17.4075 | 5.969 | 120 | 11.4385 | 0 | 16.8 | 5.3615 | 5.3615 |  | 1.05 | 16
| Sн. MV, МVА | 16+16 | 7422 | 3146 | 8.0612 | 5.969 |  | 2.0922 | 0 | 16.8 | 14.7078 |  |  | 1.05 | 16
| Sн. LV, МVА | 16+16 | 8897 | 2913 | 9.3617 | 0 |  | 9.3617 | 0 | 16.8 | 7.4383 |  |  | 1.05 | 16
75 | SS-110/35/6kv Shebekino | 40+40 | 27508 | 12250 | 30.1123 | 16.65 | 120 | 13.4623 | 0 | 42 | 28.5377 | 28.5377 |  | 1.05 | 40
| Sн. MV, МVА | 40+40 | 15624 | 7736 | 17.4343 | 11.682 |  | 5.7523 | 0 | 42 | 36.2477 |  |  | 1.05 | 40
| Sн. LV, МVА | 40+40 | 11884 | 4514 | 12.7124 | 4.968 |  | 7.7444 | 0 | 42 | 34.2556 |  |  | 1.05 | 40
76 | SS-110/10kv Sheino | 3,2+10 | 2394 | 805 | 2.5257 | 0 |  | 2.5257 | 0 | 3.36 | 0.83428 | 0.83428 |  | 1.05 | 3.2
77 | SS-110/10/6kv Yuzhnaya | 40+40 | 44406 | 12168 | 46.0429 | 12.94 | 120 | 33.1029 | 0 | 42 | 8.8971 | 8.8971 |  | 1.05 | 40
| Sн. MV, МVА | 40+40 | 7092 | 1440 | 7.2367 | 3.42 |  | 3.8167 | 0 | 42 | 38.1833 |  |  | 1.05 | 40
| Sн. LV, МVА | 40+40 | 37314 | 10728 | 38.8256 | 9.52 |  | 29.3056 | 0 | 42 | 12.6944 |  |  | 1.05 | 40
78 | SS-35/10kv Aleynikovo | 2,5+2,5 | 776 | 312 | 0.83637 | 0.43267 | 120 | 0.40371 | 0 | 2.625 | 2.2213 | 2.2213 |  | 1.05 | 2.5
79 | SS-35/10kv Alexeevka (yak.) | 2,5+2,5 | 928 | 280 | 0.96932 | 0.46639 | 120 | 0.50293 | 0 | 2.625 | 2.1221 | 2.1221 |  | 1.05 | 2.5
80 | SS-35/10kv Alexeevka (kor.) | 4+4 | 872 | 312 | 0.92614 | 0 |  | 0.92614 | 0 | 4.2 | 3.2739 | 3.2739 |  | 1.05 | 4
81 | SS-35/10kv Annovka | 2,5+2,5 | 1014 | 366 | 1.078 | 0.44652 | 80 | 0.63151 | 0 | 2.625 | 1.9935 | 1.9935 |  | 1.05 | 2.5
82 | SS-35/10kv Artelnoe | 6,3+6,3 | 3332 | 2520 | 4.1776 | 0.55 | 45 | 3.6276 | 0 | 6.615 | 2.9874 | 2.9874 |  | 1.05 | 6.3
83 | SS-35/10kv B.Dvory | 4+4 | 2632 | 912 | 2.7855 | 1.191 | 120 | 1.5945 | 0 | 4.2 | 2.6055 | 2.6055 |  | 1.05 | 4
84 | SS-35/10kv B.Ivanovka | 4+4 | 1136 | 448 | 1.2211 | 0.62488 | 80 | 0.59627 | 0 | 4.2 | 3.6037 | 3.6037 |  | 1.05 | 4
85 | SS-35/10kv B.Kolodez | 2,5+2,5 | 1032 | 420 | 1.1142 | 0.44779 | 45 | 0.6664 | 0 | 2.625 | 1.9586 | 1.9586 |  | 1.05 | 2.5
86 | SS-35/10kv B.Ples | 2,5+2,5 | 808 | 408 | 0.90517 | 0.606 | 45 | 0.29917 | 0 | 2.625 | 2.3258 | 2.3258 |  | 1.05 | 2.5
87 | SS-35/10kv B.Troitsa | 6,3+6,3 | 3564 | 1236 | 3.7722 | 2.83 | 45 | 0.94224 | 0 | 6.615 | 5.6728 | 5.6728 |  | 1.05 | 6.3
88 | SS-35/10kv Belovskoe | 4+4 | 3592 | 1632 | 3.9454 | 1.21 | 80 | 2.7354 | 0 | 4.2 | 1.4646 | 1.4646 |  | 1.05 | 4
89 | SS-35/10kv Belyanka | 2,5+4 | 1936 | 800 | 2.0948 | 1.3214 | 45 | 0.77338 | 0 | 2.625 | 1.8516 | 1.8516 |  | 1.05 | 2.5
90 | SS-35/10kv Bessonovka | 6,3+6,3 | 6464 | 2896 | 7.0831 | 0.918 | 120 | 6.1651 | 0 | 6.615 | 0.44991 | 0.44991 |  | 1.05 | 6.3
91 | SS-35/10kv B.Lubyanki | 2,5+1,6 | 1208 | 368 | 1.2628 | 0.522 | 45 | 0.74081 | 0 | 1.68 | 0.93919 | 0.93919 |  | 1.05 | 1.6
92 | SS-35/10kv V.Mikhailovka | 4+4 | 2544 | 1200 | 2.8128 | 1.45 | 80 | 1.3628 | 0 | 4.2 | 2.8372 | 2.8372 |  | 1.05 | 4
93 | SS-35/10kv Varvarovka | 2,5+2,5 | 1820 | 844 | 2.0062 | 1.0795 | 120 | 0.92663 | 0 | 2.625 | 1.6984 | 1.6984 |  | 1.05 | 2.5
94 | SS-35/10kv Vengerovka | 2,5+2,5 | 1056 | 324 | 1.1046 | 0.4 | 120 | 0.70459 | 0 | 2.625 | 1.9204 | 1.9204 |  | 1.05 | 2.5
95 | SS-35/10kv Verkhopenye | 2,5+4 | 1448 | 640 | 1.5831 | 1.0177 | 45 | 0.56548 | 0 | 2.625 | 2.0595 | 2.0595 |  | 1.05 | 2.5
96 | SS-35/10kv Viktoropol | 2,5+4 | 1328 | 456 | 1.4041 | 0.95536 | 120 | 0.44875 | 0 | 2.625 | 2.1762 | 2.1762 |  | 1.05 | 2.5
97 | SS-35/10kv Vislaya Dubrava | 4+4 | 2616 | 756 | 2.723 | 0.616 | 80 | 2.107 | 0 | 4.2 | 2.093 | 2.093 |  | 1.05 | 4
98 | SS-35/10kv Vladimirovka | 4+4 | 645 | 391 | 0.75426 | 0 |  | 0.75426 | 0 | 4.2 | 3.4457 | 3.4457 |  | 1.05 | 4
99 | SS-35/10kv Water storage | 4+6,3 | 2136 | 420 | 2.1769 | 0.305 | 45 | 1.8719 | 0 | 4.2 | 2.3281 | 2.3281 |  | 1.05 | 4
100 | SS-35/6kv Vostochnaya | 6,3+6,3 | 4320 | 1469 | 4.5629 | 1.43 | 120 | 3.1329 | 0 | 6.615 | 3.4821 | 3.4821 |  | 1.05 | 6.3
101 | SS-35/10kv Vsesvyatka | 2,5+2,5 | 1926 | 774 | 2.0757 | 0.99513 | 120 | 1.0806 | 0 | 2.625 | 1.5444 | 1.5444 |  | 1.05 | 2.5
102 | SS-35/10kv Glinnoe | 6,3+6,3 | 2432 | 1600 | 2.9111 | 1.4036 | 80 | 1.5075 | 0 | 6.615 | 5.1075 | 5.1075 |  | 1.05 | 6.3
103 | SS-35/10kv Golovchino | 2,5+2,5 | 2688 | 996 | 2.8666 | 0.617 | 45 | 2.2496 | 0 | 2.625 | 0.37541 | 0.37541 |  | 1.05 | 2.5
104 | SS-35/10kv Gora-Podol | 2,5+4 | 1504 | 516 | 1.5901 | 0.9085 | 45 | 0.68155 | 0 | 2.625 | 1.9434 | 1.9434 |  | 1.05 | 2.5
105 | SS-35/10kv Gorodishche | 4+4 | 3232 | 1600 | 3.6064 | 0 |  | 3.6064 | 0 | 4.2 | 0.59364 | 0.59364 |  | 1.05 | 4
106 | SS-35/10kv Dmitrievka | 4+4 | 1200 | 528 | 1.311 | 0.78237 | 80 | 0.52865 | 0 | 4.2 | 3.6713 | 3.6713 |  | 1.05 | 4
107 | SS-35/10kv Dorogoshch | 4+4 | 2600 | 936 | 2.7633 | 1.054 | 45 | 1.7093 | 0 | 4.2 | 2.4907 | 2.4907 |  | 1.05 | 4
108 | SS-35/10kv Dragunka | 2,5+2,5 | 912 | 352 | 0.97757 | 0.62999 | 80 | 0.34758 | 0 | 2.625 | 2.2774 | 2.2774 |  | 1.05 | 2.5
109 | SS-35/10kv Zhuravlevka | 2,5+4 | 1216 | 336 | 1.2616 | 0.274 | 80 | 0.98757 | 0 | 2.625 | 1.6374 | 1.6374 |  | 1.05 | 2.5
110 | SS-35/6kv Zhuravliki | 10+10 | 7464 | 2112 | 7.7571 | 4.051 | 120 | 3.7061 | 0 | 10.5 | 6.7939 | 6.7939 |  | 1.05 | 10
111 | SS-35/10kv Zavidovka | 2,5+2,5 | 606 | 282 | 0.6684 | 0.42 | 80 | 0.2484 | 0 | 2.625 | 2.3766 | 2.3766 |  | 1.05 | 2.5
112 | SS-35/6kv Zapadnaya | 10+10+10 | 6552 | 3360 | 7.3633 | 1.707 | 120 | 5.6563 | 0 | 21 | 15.3437 | 15.3437 |  | 1.05 | 20
113 | SS-35/10kv Zozuli | 6,3+6,3 | 5744 | 3088 | 6.5214 | 3.88 | 80 | 2.6414 | 0 | 6.615 | 3.9736 | 3.9736 |  | 1.05 | 6.3
114 | SS-35/10kv Ivitsa | 2,5+2,5 | 1192 | 392 | 1.2548 | 0.58603 | 80 | 0.66877 | 0 | 2.625 | 1.9562 | 1.9562 |  | 1.05 | 2.5
115 | SS-35/10kv Ilovka | 4+4 | 2872 | 904 | 3.0109 | 2.056 | 45 | 0.95491 | 0 | 4.2 | 3.2451 | 3.2451 |  | 1.05 | 4
116 | SS-35/10kv Istobnoe | 4+2,5 | 1224 | 632 | 1.3775 | 0.93935 | 120 | 0.43818 | 0 | 2.625 | 2.1868 | 2.1868 |  | 1.05 | 2.5
117 | SS-35/10kv Kazatskaya | 2,5+4 | 1589 | 525 | 1.6735 | 0.87141 | 45 | 0.80207 | 0 | 2.625 | 1.8229 | 1.8229 |  | 1.05 | 2.5
118 | SS-35/10kv Kazinka | 4+4 | 2412 | 672 | 2.5039 | 0.736 | 120 | 1.7679 | 0 | 4.2 | 2.4321 | 2.4321 |  | 1.05 | 4
119 | SS-35/10kv Kamyshevatoe | 2,5+2,5 | 1040 | 360 | 1.1005 | 0.712 | 120 | 0.38855 | 0 | 2.625 | 2.2365 | 2.2365 |  | 1.05 | 2.5
120 | SS-35/10kv Kirovskaya | 6,3+6,3 | 3132 | 1536 | 3.4884 | 0.7035 | 120 | 2.7849 | 0 | 6.615 | 3.8301 | 3.8301 |  | 1.05 | 6.3
121 | SS-35/10kv Kotovo | 2,5+2,5 | 2672 | 768 | 2.7802 | 1.648 | 20 | 1.1322 | 0 | 2.625 | 1.4928 | 1.4928 |  | 1.05 | 2.5
122 | SS-35/10kv Kochetovka | 2,5+4 | 858 | 294 | 0.90697 | 0.6286 | 45 | 0.27838 | 0 | 2.625 | 2.3466 | 2.3466 |  | 1.05 | 2.5
123 | SS-35/10kv Krasnoe | 4+2,5 | 1128 | 424 | 1.2051 | 1.1395 | 80 | 0.065535 | 0 | 2.625 | 2.5595 | 2.5595 |  | 1.05 | 2.5
124 | SS-35/10kv Kretovo | 4+2,5 | 1096 | 508 | 1.208 | 0.67818 | 120 | 0.52983 | 0 | 2.625 | 2.0952 | 2.0952 |  | 1.05 | 2.5
125 | SS-35/10kv Kurasovka | 4+4 | 2800 | 1168 | 3.0338 | 1.797 | 80 | 1.2368 | 0 | 4.2 | 2.9632 | 2.9632 |  | 1.05 | 4
126 | SS-35/6kv Lebedi | 4+5,6 | 4392 | 1469 | 4.6312 | 0.581 | 120 | 4.0502 | 0 | 4.2 | 0.14984 | 0.14984 |  | 1.05 | 4
127 | SS-35/6kv Ledovaya | 4+4 | 2578 | 1325 | 2.8986 | 1.321 | 80 | 1.5776 | 0 | 4.2 | 2.6224 | 2.6224 |  | 1.05 | 4
128 | SS-35/10kv Livenka | 4+4 | 3360 | 2364 | 4.1083 | 1.541 | 120 | 2.5673 | 0 | 4.2 | 1.6327 | 1.6327 |  | 1.05 | 4
129 | SS-35/10kv Lubyanoe | 2,5+2,5 | 828 | 336 | 0.89358 | 0.66672 | 80 | 0.22686 | 0 | 2.625 | 2.3981 | 2.3981 |  | 1.05 | 2.5
130 | SS-35/10kv M.Pristan | 6,3+6,3 | 6264 | 2844 | 6.8794 | 1.81 | 45 | 5.0694 | 0 | 6.615 | 1.5456 | 1.5456 |  | 1.05 | 6.3
131 | SS-35/10kv М.Troitsa | 2,5+2,5 | 568 | 368 | 0.67679 | 0.60716 | 80 | 0.069632 | 0 | 2.625 | 2.5554 | 2.5554 |  | 1.05 | 2.5
132 | SS-35/10kv Malinovka | 10+10 | 5808 | 3776 | 6.9276 | 1.357 | 120 | 5.5706 | 0 | 10.5 | 4.9294 | 4.9294 |  | 1.05 | 10
133 | SS-35/10kv Mandrovo | 2,5+2,5 | 1488 | 438 | 1.5511 | 0.65565 | 80 | 0.89548 | 0 | 2.625 | 1.7295 | 1.7295 |  | 1.05 | 2.5
134 | SS-35/10kv Mukhouderovka | 2,5+2,5 | 1362 | 510 | 1.4544 | 0.643 | 80 | 0.81135 | 0 | 2.625 | 1.8136 | 1.8136 |  | 1.05 | 2.5
135 | SS-35/10kv N.Alexandrovka | 2,5+2,5 | 1110 | 522 | 1.2266 | 0.59315 | 120 | 0.63346 | 0 | 2.625 | 1.9915 | 1.9915 |  | 1.05 | 2.5
136 | SS-35/10kv N.Derevnya | 6,3+6,3 | 5888 | 1920 | 6.1931 | 2.78 | 120 | 3.4131 | 0 | 6.615 | 3.2019 | 3.2019 |  | 1.05 | 6,3
137 | SS-35/10kv N.Tavolzhanka | 6,3+6,3 | 3360 | 912 | 3.4816 | 0.842 | 45 | 2.6396 | 0 | 6.615 | 3.9754 | 3.9754 |  | 1.05 | 6.3
138 | SS-35/10kv N.Ukolovo | 4+2,5 | 1608 | 764 | 1.7803 | 0.57 | 80 | 1.2103 | 0 | 2.625 | 1.4147 | 1.4147 |  | 1.05 | 2.5
139 | SS-35/10kv N.Khutornoe | 2,5+4 | 294 | 142 | 0.3265 | 0.19 | 80 | 0.1365 | 0 | 2.625 | 2.4885 | 2.4885 |  | 1.05 | 2.5
140 | SS-35/10kv Neminushchee | 4+2,5 | 1474 | 706 | 1.6344 | 0.65147 | 80 | 0.98288 | 0 | 2.625 | 1.6421 | 1.6421 |  | 1.05 | 2.5
141 | SS-35/10kv Nechaevka | 4+4 | 1328 | 392 | 1.3846 | 0.451 | 120 | 0.93365 | 0 | 4.2 | 3.2664 | 3.2664 |  | 1.05 | 4
142 | SS-35/10kv Nikitovka | 2,5+2,5 | 1888 | 744 | 2.0293 | 1.4354 | 80 | 0.59387 | 0 | 2.625 | 2.0311 | 2.0311 |  | 1.05 | 2.5
143 | SS-35/10kv Novenkoe | 4+4 | 2216 | 964 | 2.4166 | 1.7332 | 80 | 0.68339 | 0 | 4.2 | 3.5166 | 3.5166 |  | 1.05 | 4
144 | SS-35/10kv Oktyabrskaya | 6,3+6,3 | 7040 | 2384 | 7.4327 | 0.872 | 80 | 6.5607 | 0 | 6.615 | 0.054298 | 0.054298 |  | 1.05 | 6.3
145 | SS-35/10kv Orlik | 4+4 | 2172 | 768 | 2.3038 | 0.553 | 80 | 1.7508 | 0 | 4.2 | 2.4492 | 2.4492 |  | 1.05 | 4
146 | SS-35/10kv Podolkhi | 2,5+2,5 | 1528 | 664 | 1.666 | 1.1225 | 45 | 0.54355 | 0 | 2.625 | 2.0815 | 2.0815 |  | 1.05 | 2.5
147 | SS-35/10kv Popovka | 6,3+4 | 1152 | 528 | 1.2672 | 0.64636 | 80 | 0.62088 | 0 | 4.2 | 3.5791 | 3.5791 |  | 1.05 | 4
148 | SS-35/10kv Prelestnoe | 4+4 | 2268 | 780 | 2.3984 | 0 |  | 2.3984 | 0 | 4.2 | 1.8016 | 1.8016 |  | 1.05 | 4
149 | SS-35/6kv Privokzalnaya | 6,3+6,3 | 5357 | 2160 | 5.7761 | 0 |  | 5.7761 | 0 | 6.615 | 0.83892 | 0.83892 |  | 1.05 | 6.3
150 | SS-35/10kv Prilepy | 2,5+2,5 | 544 | 360 | 0.65233 | 0.37638 | 80 | 0.27596 | 0 | 2.625 | 2.349 | 2.349 |  | 1.05 | 2.5
151 | SS-35/10kv Printsevka | 2,5+2,5 | 1502 | 424 | 1.5607 | 0.352 | 120 | 1.2087 | 0 | 2.625 | 1.4163 | 1.4163 |  | 1.05 | 2.5
152 | SS-35/10kv Radkovka | 6,3+6,3 | 2624 | 992 | 2.8053 | 0.164 | 45 | 2.6413 | 0 | 6.615 | 3.9737 | 3.9737 |  | 1.05 | 6.3
153 | SS-35/10kv Razdornoe | 2,5+2,5 | 1314 | 576 | 1.4347 | 0.662 | 80 | 0.7727 | 0 | 2.625 | 1.8523 | 1.8523 |  | 1.05 | 2.5
154 | SS-35/10kv Repyakhovka | 2,5+2,5 | 1464 | 736 | 1.6386 | 0.88491 | 80 | 0.75368 | 0 | 2.625 | 1.8713 | 1.8713 |  | 1.05 | 2.5
155 | SS-35/10kv Rzhevka | 10+10 | 6576 | 3408 | 7.4066 | 2.53 | 45 | 4.8766 | 0 | 10.5 | 5.6234 | 5.6234 |  | 1.05 | 10
156 | SS-35/10kv Rovenki | 4+4 | 3240 | 1272 | 3.4807 | 1.7393 | 120 | 1.7414 | 0 | 4.2 | 2.4586 | 2.4586 |  | 1.05 | 4
157 | SS-35/10kv Rogovatoe | 2,5+2,5 | 1536 | 720 | 1.6964 | 0 |  | 1.6964 | 0 | 2.625 | 0.92862 | 0.92862 |  | 1.05 | 2.5
158 | SS-35/10kv Saprykino | 2,5+2,5 | 384 | 192 | 0.42933 | 0.22751 | 120 | 0.20181 | 0 | 2.625 | 2.4232 | 2.4232 |  | 1.05 | 2.5
159 | SS-35/6kv Severnaya | 6,3+6,3 | 6264 | 1887 | 6.5421 | 4.8049 | 120 | 1.7371 | 0 | 6.615 | 4.8779 | 4.8779 |  | 1.05 | 6.3
160 | SS-35/10kv Setishche | 2,5+2,5 | 1830 | 852 | 2.0186 | 1.0621 | 80 | 0.9565 | 0 | 2.625 | 1.6685 | 1.6685 |  | 1.05 | 2.5
161 | SS-35/10kv Slonovka | 4+4 | 2224 | 1392 | 2.6237 | 1.1306 | 120 | 1.4931 | 0 | 4.2 | 2.7069 | 2.7069 |  | 1.05 | 4
162 | SS-35/6kv St.Oskol -2 | 16+16 | 11806 | 4574 | 12.6611 | 1.21 | 80 | 11.4511 | 0 | 16.8 | 5.3489 | 5.3489 |  | 1.05 | 16
163 | SS-35/10kv Starikovo | 4+4 | 1464 | 660 | 1.6059 | 1.3453 | 45 | 0.26059 | 0 | 4.2 | 3.9394 | 3.9394 |  | 1.05 | 4
164 | SS-35/10kv Tavrovo | 10+10 | 8592 | 1296 | 8.6892 | 0.531 | 45 | 8.1582 | 0 | 10.5 | 2.3418 | 2.3418 |  | 1.05 | 10
165 | SS-35/10kv Terebrino | 2,5+2,5 | 1116 | 636 | 1.2845 | 0.44978 | 80 | 0.83472 | 0 | 2.625 | 1.7903 | 1.7903 |  | 1.05 | 2.5
166 | SS-35/10kv Urazovo | 6,3+6,3 | 4776 | 1524 | 5.0133 | 1.39 | 120 | 3.6233 | 0 | 6.615 | 2.9917 | 2.9917 |  | 1.05 | 6.3
167 | SS-35/10kv Utochka | 1,6+2,5 | 682 | 272 | 0.73424 | 0.47242 | 80 | 0.26182 | 0 | 1.68 | 1.4182 | 1.4182 |  | 1.05 | 1.6
168 | SS-35/6kv Fedoseevka | 4+4 | 2160 | 682 | 2.2651 | 0 |  | 2.2651 | 0 | 4.2 | 1.9349 | 1.9349 |  | 1.05 | 4
169 | SS-35/10kv Foshchevatvo | 1,6+2,5 | 980 | 408 | 1.0615 | 0.78681 | 45 | 0.27473 | 0 | 1.68 | 1.4053 | 1.4053 |  | 1.05 | 1.6
170 | SS-35/10kv Kholodnoe | 4+4 | 1708 | 516 | 1.7842 | 0 |  | 1.7842 | 0 | 4.2 | 2.4158 | 2.4158 |  | 1.05 | 4
171 | SS-35/6kv Chernyansky sugar plant | 7,5+6,3 | 1608 | 1128 | 1.9642 | 1.3513 | 20 | 0.61293 | 0 | 6.615 | 6.0021 | 6.0021 |  | 1.05 | 6.3
172 | SS-35/10kv Shatalovka | 6,3+6,3 | 1928 | 736 | 2.0637 | 0 |  | 2.0637 | 0 | 6.615 | 4.5513 | 4.5513 |  | 1.05 | 6.3
173 | SS-35/10kv Shakhovka | 2,5+2,5 | 1596 | 588 | 1.7009 | 0.79066 | 80 | 0.91021 | 0 | 2.625 | 1.7148 | 1.7148 |  | 1.05 | 2.5
174 | SS-35/10kv Shishino | 4+6,3 | 3456 | 904 | 3.5723 | 1.03 | 80 | 2.5423 | 0 | 4.2 | 1.6577 | 1.6577 |  | 1.05 | 4
175 | SS-35/10kv Yablonovo | 4+4 | 1664 | 688 | 1.8006 | 1.1284 | 80 | 0.6722 | 0 | 4.2 | 3.5278 | 3.5278 |  | 1.05 | 4
176 | SS-35/10kv Yarskoe | 2,5+2,5 | 504 | 264 | 0.56896 | 0.14648 | 80 | 0.42248 | 0 | 2.625 | 2.2025 | 2.2025 |  | 1.05 | 2.5
| TOTAL: | 3186.9 |  |  | 1131.8395 | #VALUE! |  | #VALUE! | [5 empty] | 1.05
| deficit | [10 empty] | -2.449 |  | 1.05
| proficit | [10 empty] | 897.8224 |  | 1.05

## МРСК 2
Calculation of transmission capacity of Main substations of the branch "Belgorodenergo" of IDGC of Centre, JSC following the results of winter measurement of peak load of 2009.
Table 2
No. | Object of main substation, voltage class | Expected deficit/proficit | [9 empty] | Note | Примечание
|  | Installed power capacity of transformers Sуst. Including their number, pcs/ MVA | Additional capacity according to provided technical specifications at TS, MVA | Expected load of Main substation, MVA | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit/proficit of Main Substation, MVA
[5 empty] | MVA | Min
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
One-transformer substations
1 | SS-110/35/10kv D.Polyana | 6.3 | 0 | 1.6675 | 1.457 | 45 | 0.2105 | 0 | 1.457 | -0.2105 | -0.57942 |  |  |  | 0 | 6.3
| Sн. MV, МVА | 6.3 | 0 | 0.59479 | 0.958 |  | -0.36321 | 0 | 0.958 | 0.36321 |  |  |  |  | 0 | 0
| Sн. LV, МVА | 6.3 | 0 | 1.0784 | 0.499 |  | 0.57942 | 0 | 0.499 | -0.57942 |  |  |  |  | 0 | 0
2 | SS-110/35/10kv Konshino | 6.3 | 0 | 0.40539 | 0.39 | 20 | 0.01539 | 0 | 0.39 | -0.01539 | -0.01539 |  |  |  | 0 | 6.3
| Sн. MV, МVА | 6.3 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
| Sн. LV, МVА | 6.3 | 0 | 0.40539 | 0.39 |  | 0.01539 | 0 | 0.39 | -0.01539 |  |  |  |  | 0 | 0
3 | SS-110/35/10kv Orositelnaya | 16 | 0 | 12.2322 | 11.607 | 120 | 0.62525 | 0 | 11.607 | -0.62525 | -0.90525 |  |  |  |  | 16
| Sн. MV, МVА | 16 | 0 | 9.5113 | 8.606 |  | 0.90525 | 0 | 8.606 | -0.90525 |  |  |  |  | 0 | 0
| Sн. LV, МVА | 16 | 0 | 2.825 | 3.001 |  | -0.176 | 0 | 3.001 | 0.176 |  |  |  |  | 0 | 0
4 | SS-110/35/6kv Pishcheprom | 25 | 1.267 | 7.5801 | 6.679 | 120 | 0.90114 | 0 | 6.679 | -0.90114 | -0.90114 |  |  |  | 1.267 | 25
| Sн. MV, МVА | 12.5 | 0 | 2.2697 | 2.022 |  | 0.24769 | 0 | 2.022 | -0.24769 |  |  |  |  | 0 | 0
| Sн. LV, МVА | 12.5 | 1.267 | 5.3105 | 4.657 |  | 0.65346 | 0 | 4.657 | -0.65346 |  |  |  |  | 0 | 0
5 | SS-110/35/10kv Rovenki | 16 | 0.709 | 3.349 | 3.44 | 120 | -0.090965 | 0 | 3.44 | 0.090965 | 0.090965 |  |  |  |  | 16
| Sн. MV, МVА | 16 | 0.614 | 0.64806 | 4 |  | -3.3519 | 0 | 4 | 3.3519 |  |  |  |  | 0.614 | 0
| Sн. LV, МVА | 16 | 0.095 | 2.7208 | 3.44 |  | -0.71921 | 0 | 3.44 | 0.71921 |  |  |  |  | 0.095 | 0
6 | SS-110/35/10kv Serebryanka | 10 | 0 | 1.2961 | 1.78 | 45 | -0.48388 | 0 | 1.78 | 0.48388 | 0 |  |  |  | 0 | 10
| Sн. MV, МVА | 10 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
| Sн. LV, MVА | 10 | 0 | 1.2961 | 1.78 |  | -0.48388 | 0 | 1.78 | 0.48388 |  |  |  |  | 0 | 0
7 | SS-35/10kv Afanasyevka | 1.6 | 0 | 0.91204 | 0.6464 | 45 | 0.26564 | 0 | 0.6464 | -0.26564 | -0.26564 |  |  |  | 0 | 1.6
8 | SS-35/10kv Borisovka | 1.6 | 0 | 0.60716 | 0.6835 | 45 | -0.076343 | 0 | 0.6835 | 0.076343 | 0.076343 |  |  |  | 0 | 1.6
9 | SS-35/10kv Borisy | 1.6 | 2.083 | 2.5743 | 0 | 20 | 2.5743 | 0 | 0 | -2.5743 | -2.5743 |  |  |  | 2.083 | 1.6
10 | SS-35/10kv Gostishchevo | 4 | 0.28 | 4.3362 | 2.64 | 80 | 1.6962 | 0 | 2.64 | -1.6962 | -1.6962 |  |  |  | 0.28 | 4
11 | SS-35/10kv Gruzskoe | 1.6 | 0 | 0.66101 | 1.05 | 80 | -0.38899 | 0 | 1.05 | 0.38899 | 0.38899 |  |  |  | 0 | 1.6
12 | SS-35/10kv Zemsnaryad | 1.6 | 0.185 | 0.2048 | 0 |  | 0.2048 | 0 | 0 | -0.2048 | -0.2048 |  |  |  | 0.185 | 1.6
13 | SS-35/10kv Kazachya Lisitsa | 2.5 | 0 | 0.37702 | 0 |  | 0.37702 | 0 | 0 | -0.37702 | -0.37702 |  |  |  | 0 | 2.5
14 | SS-35/10kv Kamyzino | 2.5 | 0 | 1.0666 | 0.541 | 45 | 0.52564 | 0 | 0.541 | -0.52564 | -0.52564 |  |  |  | 0 | 2.5
15 | SS-35/10kv Koloskovo | 2.5 | 0.025 | 2.1201 | 1.6626 | 45 | 0.45748 | 0 | 1.6626 | -0.45748 | -0.45748 |  |  |  | 0.025 | 2.5
16 | SS-35/10jkv Kryukovo | 2.5 | 0 | 1.6587 | 1.55 | 45 | 0.10865 | 0 | 1.55 | -0.10865 | -0.10865 |  |  |  | 0 | 2.5
17 | SS-35/10kv Kushchino | 1.6 | 0 | 0.41011 | 0.4101 | 80 | 1.218e-05 | 0 | 0.4101 | -1.218e-05 | -1.218e-05 |  |  |  | 0 | 1.6
18 | SS-35/10kv Lopukhinka | 2.5 | 0 | 0.416 | 0.407 | 20 | 0.009 | 0 | 0.407 | -0.009 | -0.009 |  |  |  | 0 | 2.5
19 | SS-35/10kv Malakeevo | 2.5 | 0.014 | 1.463 | 1.38 | 120 | 0.082972 | 0 | 1.38 | -0.082972 | -0.082972 |  |  |  | 0.014 | 2.5
20 | SS-35/10kv Murom | 2.5 | 0 | 1.4041 | 1.54 | 45 | -0.13589 | 0 | 1.54 | 0.13589 | 0.13589 |  |  |  | 0 | 2.5
21 | SS-35/10kv Nikolaevka | 2.5 | 0 | 0.72377 | 0.6647 | 45 | 0.059068 | 0 | 0.6647 | -0.059068 | -0.059068 |  |  |  | 0 | 2.5
22 | SS-35/10kv Nikolskoe | 4 | 0.2421 | 2.0617 | 0.78 | 120 | 1.2817 | 0 | 0.78 | -1.2817 | -1.2817 |  |  |  | 0.2421 | 4
23 | SS-35/10kv Pokrovka | 4 | 0.013 | 0.78194 | 0.722 | 45 | 0.059937 | 0 | 0.722 | -0.059937 | -0.059937 |  |  |  | 0.013 | 4
24 | SS-35/10kv Pyatnitskoe | 4 | 0.035 | 2.594 | 1.84 | 80 | 0.75397 | 0 | 1.84 | -0.75397 | -0.75397 |  |  |  | 0.035 | 4
25 | SS-35/10kv Sugar plant Ivnya | 2.5 | 0 | 0.17787 | 1.676 | 80 | -1.4981 | 0 | 1.676 | 1.4981 | 1.4981 |  |  |  | 0 | 2.5
26 | SS-35/10kv Svistovka | 2.5 | 0.035 | 0.72193 | 0.6872 | 45 | 0.034729 | 0 | 0.6872 | -0.034729 | -0.034729 |  |  |  | 0.035 | 2.5
27 | SS-35/10kv sovkhoz "Urazovsky" | 2.5 | 0 | 0.72999 | 0.7238 | 120 | 0.0061863 | 0 | 0.7238 | -0.0061863 | -0.0061863 |  |  |  | 0 | 2.5
28 | SS-35/10kv Kharkovskaya | 2.5 | 0 | 0.72665 | 0.6797 | 120 | 0.046947 | 0 | 0.6797 | -0.046947 | -0.046947 |  |  |  | 0 | 2.5
29 | SS-35/10kv Tserkovnaya | 2.5 | 0 | 1.1487 | 1 | 80 | 0.14869 | 0 | 1 | -0.14869 | -0.14869 |  |  |  | 0 | 2.5
Two- and more transformer substations | [14 empty] | 0 | 137.7
30 | SS-110/6kv Automobile maintenance plant | 16+16 | 0.952 | 16.4413 | 3.561 | 45 | 12.8803 | 0 | 16.8 | 3.9197 | 3.9197 |  | 1.05 | 16 | 0.952 | 16+16 | 32
31 | SS-110/35/10kv Aydar | 16+10 | 0.03 | 9.8331 | 8.95 | 120 | 0.88307 | 0 | 10.5 | 9.6169 | 9.6169 |  | 1.05 | 10 | 0.03 | 16+10 | 26
| Sн. MV, МVА | 16+10 | 0 | 8.1484 | 7.29 |  | 0.85843 | 0 | 10.5 | 9.6416 |  |  | 1.05 | 10 | 0 | 0
| Sн. LV, МVА | 16+10 | 0.03 | 1.6864 | 1.66 |  | 0.026407 | 0 | 10.5 | 10.4736 |  |  | 1.05 | 10 | 0 | 0
32 | SS-110/35/10kv Alexandrovka | 16+16 | 12.3214 | 25.4529 | 8.37 | 80 | 17.0829 | 0 | 16.8 | -0.28293 | -0.28293 |  | 1.05 | 16 | 12.3214 | 16+16 | 32
| Sн. MV, МVА | 16+16 | 0 | 6.952 | 6.697 |  | 0.25498 | 0 | 16.8 | 16.545 |  |  | 1.05 | 16 | 0 | 0
| Sн. LV, МVА | 16+16 | 12.3214 | 18.501 | 1.673 |  | 16.828 | 0 | 16.8 | -0.027957 |  |  | 1.05 | 16 | 11.963 | 0
33 | SS-110/35/10kv Alexeevka | 25+25+25 | 0 | 43.4741 | 5.322 | 120 | 38.1521 | 0 | 52.5 | 14.3479 | 14.3479 |  | 1.05 | 41 |  | 25+25+25 | 75
| Sн. MV, МVА | 25+25+25 | 0 | 19.0616 | 3.102 |  | 15.9596 | 0 | 52.5 | 36.5404 |  |  | 1.05 | 41 | 0 | 0
| Sн. LV, МVА | 25+25+25 | 1.3985 | 25.8667 | 2.22 |  | 23.6467 | 0 | 52.5 | 28.8533 |  |  | 1.05 | 41 | 1.3985 | 0
34 | SS-110/35/10kv Arkhangelskoe | 10+16 | 0.015 | 10.7761 | 8.87 | 45 | 1.9061 | 0 | 10.5 | 8.5939 | 8.5939 |  | 1.05 | 10 | 0.015 | 10+16 | 26
| Sн. MV, МVА | 10+16 | 0 | 10.1449 | 8.867 |  | 1.2779 | 0 | 10.5 | 9.2221 |  |  | 1.05 | 10 | 0 | 0
| Sн. LV, МVА | 10+16 | 0.015 | 0.63303 | 0 |  | 0.63303 | 0 | 10.5 | 9.867 |  |  | 1.05 | 10 | 0 | 0
35 | SS-110/6kv Belgorod-1 | 40+48 | 0.747 | 45.4865 | 0 | 120 | 45.4865 | 0 | 42 | -3.4865 | -3.4865 |  | 1.05 | 40 | 0.747 | 40+48 | 88
36 | SS-110/35/10kv Borisovka | 16+16 | 0 | 12.2392 | 11.433 | 120 | 0.80621 | 0 | 16.8 | 15.9938 | 4.8082 |  | 1.05 | 16 |  | 16+16 | 32
| Sн. MV, МVА | 16+8 | 0 | 5.4268 | 8.133 |  | -2.7062 | 0 | 8.4 | 11.1062 |  |  | 1.05 | 8 | 0 | 0
| Sн. LV, МVА | 16+8 | 0.038 | 6.8918 | 3.3 |  | 3.5918 | 0 | 8.4 | 4.8082 |  |  | 1.05 | 8 | 0.038 | 0
37 | SS-110/35/10kv V.Pokrovka | 10+10 | 0 | 10.3847 | 11.5 | 120 | -1.1153 | 0 | 10.5 | 11.6153 | 9.4887 |  | 1.05 | 10 |  | 10+10 | 20
| Sн. MV, МVА | 10+10 | 0 | 8.8113 | 7.8 |  | 1.0113 | 0 | 10.5 | 9.4887 |  |  | 1.05 | 10 | 0 | 0
| Sн. LV, МVА | 10+10 | 0 | 1.5778 | 3.7 |  | -2.1222 | 0 | 10.5 | 12.6222 |  |  | 1.05 | 10 | 0.012 | 0
38 | SS-110/35/10kv Veydelevka | 10+10 | 0.015 | 9.6962 | 8.83 | 120 | 0.86624 | 0 | 10.5 | 9.6338 | 9.1219 |  | 1.05 | 10 |  | 10+10 | 20
| Sн. MV, МVА | 10+10 | 0 | 5.3331 | 3.955 |  | 1.3781 | 0 | 10.5 | 9.1219 |  |  | 1.05 | 10 | 0 | 0
| Sн. LV, МVА | 10+10 | 0.015 | 4.3664 | 4.875 |  | -0.50864 | 0 | 10.5 | 11.0086 |  |  | 1.05 | 10 | 0.237 | 0
39 | SS-110/6kv Vitamin plant | 25+25 | 3.656 | 18.723 | 1.46 | 45 | 17.263 | 0 | 26.25 | 8.987 | 8.987 |  | 1.05 | 25 | 3.656 | 25+25 | 50
40 | SS-110/35/10kv Volokonovka | 25+25 | 0.223 | 20.2287 | 10.651 | 120 | 9.5777 | 0 | 26.25 | 16.6723 | 16.6723 |  | 1.05 | 25 |  | 25+25 | 50
| Sн. MV, МVА | 25+25 | 0 | 11.2656 | 8.576 |  | 2.6896 | 0 | 26.25 | 23.5604 |  |  | 1.05 | 25 | 0 | 0
| Sн. LV, МVА | 25+25 | 0.223 | 8.968 | 2.075 |  | 6.893 | 0 | 26.25 | 19.357 |  |  | 1.05 | 25 | 0.223 | 0
41 | SS-110/35/6kv Vostochnaya | 25+25 | 1.8005 | 42.3913 | 25.07 | 120 | 17.3213 | 0 | 26.25 | 8.9287 | 4.4909 |  | 1.05 | 25 | 1.8005 | 25+25 | 50
| Sн. MV, МVА | 25+25 | 0 | 16.9581 | 21.3 |  | -4.3419 | 0 | 26.25 | 30.5919 |  |  | 1.05 | 25 | 0 | 0
| Sн. LV, МVА | 25+25 | 1.8005 | 25.5291 | 3.77 |  | 21.7591 | 0 | 26.25 | 4.4909 |  |  | 1.05 | 25 | 0 | 0
42 | SS-110/10/6kv Golofeevka | 25+25 | 0.25 | 2.8401 | 0 |  | 2.8401 | 0 | 26.25 | 23.4099 | 10.2849 |  | 1.05 | 25 | 0.25 | 25+25 | 50
| Sн. MV, МVА | 12,5+12,5 | 0 | 0 | 0 |  | 0 | 0 | 13.125 | 13.125 |  |  | 1.05 | 12.5 | 0 | 0
| Sн. LV, МVА | 12,5+12,5 | 0.25 | 2.8401 | 0 |  | 2.8401 | 0 | 13.125 | 10.2849 |  |  | 1.05 | 12.5 | 0.25 | 0
43 | SS-110/10kv Gotnya | 16+16 | 0.063 | 9.1941 | 6.43 | 120 | 2.7641 | 0 | 16.8 | 14.0359 | 14.0359 |  | 1.05 | 16 | 0.063 | 16+16 | 32
44 | SS-110/35/10kv Grayvoron | 16+16 | 0.03 | 14.2433 | 13.953 | 80 | 0.29034 | 0 | 16.8 | 16.5097 | 14.4201 |  | 1.05 | 16 | 0.03 | 16+16 | 32
| Sн. MV, МVА | 16+16 | 0 | 8.8207 | 10.903 |  | -2.0823 | 0 | 16.8 | 18.8823 |  |  | 1.05 | 16 | 0 | 0
| Sн. LV, МVА | 16+16 | 0.03 | 5.4299 | 3.05 |  | 2.3799 | 0 | 16.8 | 14.4201 |  |  | 1.05 | 16 | 0.03 | 0
45 | SS-110/6kv Donets | 40+40 | 2.605 | 29.7039 | 6.73 | 120 | 22.9739 | 0 | 42 | 19.0261 | 19.0261 |  | 1.05 | 40 | 2.605 | 40+40 | 80
46 | SS-110/10kv Dubovoe | 40+40 | 2.0873 | 26.321 | 11.23 | 120 | 15.091 | 0 | 42 | 26.909 | 26.909 |  | 1.05 | 40 | 2.0873 | 40+40 | 80
47 | SS-110/35/6kv Zhuravliki | 40+25 | 0.415 | 24.9848 | 12.4 | 120 | 12.5848 | 0 | 42 | 29.4152 | 29.4152 |  | 1.05 | 40 | 0.415 | 40+25 | 65
| Sн. MV, МVА | 40+25 | 0 | 17.6898 | 6.227 |  | 11.4628 | 0 | 42 | 30.5372 |  |  | 1.05 | 40 | 0 | 0
| Sн. LV, МVА | 40+25 | 0.415 | 7.3449 | 6.173 |  | 1.1719 | 0 | 42 | 40.8281 |  |  | 1.05 | 40 | 0.01 | 0
48 | SS-110/10kv Zapadnaya | 16+16 | 1.82 | 17.6263 | 1.249 | 80 | 16.3773 | 0 | 16.8 | 0.42274 | 0.42274 |  | 1.05 | 16 | 1.82 | 16+16 | 32
49 | SS-110/35/10kv Ivnya | 10+10 | 0.085 | 6.4627 | 6.16 | 80 | 0.30266 | 0 | 10.5 | 10.1973 | 10.1973 |  | 1.05 | 10 | 0.085 | 10+10 | 20
| Sн. MV, МVА | 10+10 | 0 | 2.4801 | 2.375 |  | 0.10508 | 0 | 10.5 | 10.3949 |  |  | 1.05 | 10 | 0 | 0
| Sн. LV, МVА | 10+10 | 0.085 | 3.9886 | 3.785 |  | 0.20362 | 0 | 10.5 | 10.2964 |  |  | 1.05 | 10 | 0 | 0
50 | SS-110/35/10kv K.Gvardiya | 16+16 | 0.3655 | 18.0287 | 7.7116 | 120 | 10.3171 | 0 | 16.8 | 6.4829 | 6.4829 |  | 1.05 | 16 | 0.3655 | 16+16 | 32
| Sн. MV, МVА | 16+16 | 0 | 9.8677 | 4.854 |  | 5.0137 | 0 | 16.8 | 11.7863 |  |  | 1.05 | 16 | 0 | 0
| Sн. LV, МVА | 16+16 | 0.3655 | 8.1813 | 2.8576 |  | 5.3237 | 0 | 16.8 | 11.4763 |  |  | 1.05 | 16 | 0 | 0
51 | SS-110/10/6kv Kazatskie Bugry | 25+25 | 0.015 | 13.1851 | 9.65 | 80 | 3.5351 | 0 | 26.25 | 22.7149 | 18.8264 |  | 1.05 | 25 | 0.015 | 25+25 | 50
| Sн. MV, МVА | 25+25 | 0 | 1.7668 | 1.384 |  | 0.38281 | 0 | 26.25 | 25.8672 |  |  | 1.05 | 25 | 0 | 0
| Sн. LV, МVА | 25+25 | 0.015 | 11.4236 | 4 |  | 7.4236 | 0 | 26.25 | 18.8264 |  |  | 1.05 | 25 | 0 | 0
52 | SS-110/35/10kv Korocha | 16+16+16 | 1.312 | 23.3827 | 2.019 | 20 | 21.3637 | 0 | 33.6 | 12.2363 | 12.2363 |  | 1.05 | 32 | 1.312 | 16+16+16 | 48
| Sн. MV, МVА | 16+16+16 | 0 | 8.5842 | 1.719 |  | 6.8652 | 0 | 33.6 | 26.7348 |  |  | 1.05 | 32 | 0 | 0
| Sн. LV, МVА | 16+16+16 | 1.312 | 14.805 | 0.3 |  | 14.505 | 0 | 33.6 | 19.095 |  |  | 1.05 | 32 | 0 | 0
53 | SS-110/35/10kv Krasnaya Yaruga | 10+10 | 0 | 10.5221 | 9.158 | 120 | 1.3641 | 0 | 10.5 | 9.1359 | 9.1359 |  | 1.05 | 10 | 0.111 | 10+10 | 20
| Sн. MV, МVА | 10+10 | 0 | 4.6558 | 3.52 |  | 1.1358 | 0 | 10.5 | 9.3642 |  |  | 1.05 | 10 | 0 | 0
| Sн. LV, МVА | 10+10 | 0 | 5.8665 | 5.638 |  | 0.22854 | 0 | 10.5 | 10.2715 |  |  | 1.05 | 10 |  | 0
54 | SS-110/10kv Krapivenskaya | 16+16 | 0.65 | 0.65 | 0 | 0 | 0.65 | 0 | 16.8 | 16.15 | 16.15 |  |  |  | 0.65
55 | SS-110/10/10kv Mayskaya | 40+40 | 0.035 | 2.7015 |  |  | 2.7015 | 0 | 42 | 39.2985 | 39.2985 |  | 1.05 | 16 | 0.035 | 16+16 | 80
56 | SS-110/35/10kv Maximovka | 16+16 | 0 | 8.4783 | 11.48 | 45 | -3.0017 | 0 | 16.8 | 19.8017 | 17.792 |  | 1.05 | 16 | 0 | 16+16 | 32
| Sн. MV, МVА | 16+16 | 0 | 7.4448 | 9.449 |  | -2.0042 | 0 | 16.8 | 18.8042 |  |  | 1.05 | 16 | 0 | 0
| Sн. LV, МVА | 16+16 | 0 | 1.039 | 2.031 |  | -0.99201 | 0 | 16.8 | 17.792 |  |  | 1.05 | 16 | 0 | 0
57 | SS-110/35/10kv N.Oskol | 25+31,5 | 0.305 | 23.1386 | 9.119 | 80 | 14.0196 | 0 | 26.25 | 12.2304 | 12.2304 |  | 1.05 | 25 | 0.305 | 25+31,5 | 56.5
| Sн. MV, МVА | 25+31,5 | 0 | 8.2243 | 7.83 |  | 0.39428 | 0 | 26.25 | 25.8557 |  |  | 1.05 | 25 | 0 | 0
| Sн. LV, МVА | 25+31,5 | 0.305 | 14.9436 | 1.289 |  | 13.6546 | 0 | 26.25 | 12.5954 |  |  | 1.05 | 25 | 0 | 0
58 | SS-110/10kv Obukhovskaya | 25+25 | 0 | 2.3023 | 0 |  | 2.3023 | 0 | 26.25 | 23.9477 | 23.9477 |  | 1.05 | 25 | 0 | 25+25 | 50
59 | SS-110/6kv Ochistnye | 16+16 | 0 | 5.7973 | 0 |  | 5.7973 | 0 | 16.8 | 11.0027 | 11.0027 |  | 1.05 | 16 |  | 16+16 | 32
60 | SS-110/10kv Promyshlennaya | 25+25 | 3.4417 | 20.6313 | 0 |  | 20.6313 | 0 | 26.25 | 5.6187 | 5.6187 |  | 1.05 | 25 | 3.4417 | 25+25 | 50
61 | SS-110/10kv Poultry plant | 16+16 | 3.29 | 14.7579 | 1.296 | 80 | 13.4619 | 0 | 16.8 | 3.3381 | 3.3381 |  | 1.05 | 16 | 3.29 | 16+16 | 32
62 | SS-110/10kv Pushkarnaya | 40+40 | 0.088 | 34.9096 | 0 | 60 | 34.9096 | 0 | 42 | 7.0904 | 7.0904 |  | 1.05 | 40 | 0.088 | 40+40 | 80
63 | SS-110/35/10kv Rakitnoe | 10+10 | 0.5586 | 11.458 | 8.98 | 120 | 2.478 | 0 | 10.5 | 8.022 | 7.2386 |  | 1.05 | 10 | 0.5586 | 10+10 | 20
| Sн. MV, МVА | 10+10 | 0 | 5.8644 | 6.407 |  | -0.54263 | 0 | 10.5 | 11.0426 |  |  | 1.05 | 10 | 0 | 0
| Sн. LV, МVА | 10+10 | 0.5586 | 5.8344 | 2.573 |  | 3.2614 | 0 | 10.5 | 7.2386 |  |  | 1.05 | 10 | 0 | 0
64 | SS-110/35/6kv Rudnik | 25+25 | 0.01 | 18.4653 | 10.46 | 45 | 8.0053 | 0 | 26.25 | 18.2447 | 18.2447 |  | 1.05 | 25 | 0.01 | 25+25 | 50
| Sн. MV, МVА | 25+25 | 0 | 11.547 | 10.46 |  | 1.087 | 0 | 26.25 | 25.163 |  |  | 1.05 | 25 | 0 | 0
| Sн. LV, МVА | 25+25 | 0.01 | 6.9192 | 0 |  | 6.9192 | 0 | 26.25 | 19.3308 |  |  | 1.05 | 25 | 0 | 0
65 | SS-110/10kv Severnaya | 40+40 | 2.9216 | 15.3936 | 3.312 | 45 | 12.0816 | 0 | 42 | 29.9184 | 29.9184 |  | 1.05 | 40 | 2.9216 | 40+40 | 80
66 | SS-110/35/10kv Skorodnoe | 16+16 | 0.045 | 11.9082 | 10.36 | 120 | 1.5482 | 0 | 16.8 | 15.2518 | 15.2518 |  | 1.05 | 16 | 0.045 | 16+16 | 32
| Sн. MV, МVА | 16+16 | 0 | 7.7653 | 7.562 |  | 0.20331 | 0 | 16.8 | 16.5967 |  |  | 1.05 | 16 | 0 | 0
| Sн. LV, МVА | 16+16 | 0.045 | 4.1429 | 2.798 |  | 1.3449 | 0 | 16.8 | 15.4551 |  |  | 1.05 | 16 | 0 | 0
67 | SS-110/35/6kv St.Oskol - 1 | 20+25+25 | 0.272 | 29.2855 | 0 |  | 29.2855 | 0 | 47.25 | 17.9645 | 17.9645 |  | 1.05 | 45 | 0.272 | 20+25+25 | 70
| Sн. MV, МVА | 20+25+25 | 0 | 5.7778 | 0 |  | 5.7778 | 0 | 47.25 | 41.4722 |  |  | 1.05 | 45 | 0 | 0
| Sн. LV, МVА | 20+25+25 | 0.272 | 23.516 | 0 |  | 23.516 | 0 | 47.25 | 23.734 |  |  | 1.05 | 45 | 0 | 0
68 | SS-110/35/10kv Streletskaya | 16+16 | 0.36285 | 6.6681 | 2.23 | 80 | 4.4381 | 0 | 16.8 | 12.3619 | 3.9946 |  | 1.05 | 16 | 0.36285 | 16+16 | 32
| Sн. MV, МVА | 16+8 | 0 | 0.095258 | 0 |  | 0.095258 | 0 | 8.4 | 8.3047 |  |  | 1.05 | 8 | 0 | 0
| Sн. LV, МVА | 16+8 | 0.36285 | 6.6354 | 2.23 |  | 4.4054 | 0 | 8.4 | 3.9946 |  |  | 1.05 | 8 | 0 | 0
69 | SS-110/6kv Stroitel | 15+15 | 0.587 | 16.3364 | 0 |  | 16.3364 | 0 | 15.75 | -0.58642 | -0.58642 |  | 1.05 | 15 | 0.587 | 15+15 | 30
70 | SS-110/35/10kv Tomarovka | 16+16 | 0.09 | 13.3415 | 3.46 | 45 | 9.8815 | 0 | 16.8 | 6.9185 | 6.9185 |  | 1.05 | 16 |  | 16+16 | 32
| Sн. MV, МVА | 16+16 | 0 | 4.8655 | 3.46 |  | 1.4055 | 0 | 16.8 | 15.3945 |  |  | 1.05 | 16 | 0 | 0
| Sн. LV, МVА | 16+16 | 0.09 | 8.4761 | 0 |  | 8.4761 | 0 | 16.8 | 8.3239 |  |  | 1.05 | 16 | 0.09 | 0
71 | SS-110/6kv Chemical plant | 32+32 | 0.055 | 9.2506 | 5.56 | 45 | 3.6906 | 0 | 33.6 | 29.9094 | 29.9094 |  | 1.05 | 32 | 0.055 | 32+32 | 64
72 | SS-110/10kv Tsentralnaya | 40+40 | 0.826 | 32.514 | 0 |  | 32.514 | 0 | 42 | 9.486 | 9.486 |  | 1.05 | 40 | 0.826 | 40+40 | 80
73 | SS-110/35/10kv Cheremoshnoe | 25+25 | 0.014 | 24.7341 | 20.54 | 80 | 4.1941 | 0 | 26.25 | 22.0559 | 22.0559 |  | 1.05 | 25 | 0.014 | 25+25 | 50
| Sн. MV, МVА | 25+25 | 0 | 22.9155 | 19.676 |  | 3.2395 | 0 | 26.25 | 23.0105 |  |  | 1.05 | 25 | 0 | 0
| Sн. LV, МVА | 25+25 | 0 | 1.8186 | 0 |  | 1.8186 | 0 | 26.25 | 24.4314 |  |  | 1.05 | 25 | 0 | 0
74 | SS-110/35/10kv Chernyanka | 16+16 | 0.206 | 17.6135 | 5.969 | 120 | 11.6445 | 0 | 16.8 | 5.1555 | 5.1555 |  | 1.05 | 16 | 0.206 | 16+16 | 32
| Sн. MV, МVА | 16+16 | 0 | 8.0612 | 5.969 |  | 2.0922 | 0 | 16.8 | 14.7078 |  |  | 1.05 | 16 | 0 | 0
| Sн. LV, МVА | 16+16 | 0.206 | 9.5677 | 0 |  | 9.5677 | 0 | 16.8 | 7.2323 |  |  | 1.05 | 16 | 0 | 0
75 | SS-110/35/6kv Shebekino | 40+40 | 0.149 | 30.2613 | 16.65 | 120 | 13.6113 | 0 | 42 | 28.3887 | 28.3887 |  | 1.05 | 40 | 0.149 | 40+40 | 80
| Sн. MV, МVА | 40+40 | 0 | 17.4343 | 11.682 |  | 5.7523 | 0 | 42 | 36.2477 |  |  | 1.05 | 40 | 0 | 0
| Sн. LV, МVА | 40+40 | 0.149 | 12.8614 | 4.968 |  | 7.8934 | 0 | 42 | 34.1066 |  |  | 1.05 | 40 | 0 | 0
76 | SS-110/10kv Sheino | 3,2+10 | 0.038 | 2.5637 | 0 |  | 2.5637 | 0 | 3.36 | 0.79628 | 0.79628 |  | 1.05 | 3.2 | 0.038 | 3,2+10 | 13.2
77 | SS-110/10/6kv Yuzhnaya | 40+40 | 1.73 | 47.7729 | 12.94 | 120 | 34.8329 | 0 | 42 | 7.1671 | 7.1671 |  | 1.05 | 40 | 1.73 | 40+40 | 80
| Sн. MV, МVА | 40+40 | 0 | 7.2367 | 3.42 |  | 3.8167 | 0 | 42 | 38.1833 |  |  | 1.05 | 40 | 0 | 0
| Sн. LV, МVА | 40+40 | 1.73 | 40.5556 | 9.52 |  | 31.0356 | 0 | 42 | 10.9644 |  |  | 1.05 | 40 | 0 | 0
78 | SS-35/10kv Aleynikovo | 2,5+2,5 | 0.015 | 0.85137 | 0.43267 | 120 | 0.41871 | 0 | 2.625 | 2.2063 | 2.2063 |  | 1.05 | 2.5 | 0.015 | 2,5+2,5 | 5
79 | SS-35/10kv Alexeevka (yak.) | 2,5+2,5 | 0 | 0.96932 | 0.46639 | 120 | 0.50293 | 0 | 2.625 | 2.1221 | 2.1221 |  | 1.05 | 2.5 | 0 | 2,5+2,5 | 5
80 | SS-35/10kv Alexeevka (kor.) | 4+4 | 0.06 | 0.98614 | 0 |  | 0.98614 | 0 | 4.2 | 3.2139 | 3.2139 |  | 1.05 | 2.5 | 0.06 | 4+4 | 8
81 | SS-35/10kv Annovka | 2,5+2,5 | 0.015 | 1.093 | 0.44652 | 80 | 0.64651 | 0 | 2.625 | 1.9785 | 1.9785 |  | 1.05 | 2.5 | 0.015 | 2,5+2,5 | 5
82 | SS-35/10kv Artelnoe | 6,3+6,3 | 0.015 | 4.1926 | 0.55 | 45 | 3.6426 | 0 | 6.615 | 2.9724 | 2.9724 |  | 1.05 | 6.3 | 0.015 | 6,3+6,3 | 12.6
83 | SS-35/10kv B.Dvory | 4+4 | 0.015 | 2.8005 | 1.191 | 120 | 1.6095 | 0 | 4.2 | 2.5905 | 2.5905 |  | 1.05 | 4 | 0.015 | 4+4 | 8
84 | SS-35/10kv B.Ivanovka | 4+4 | 0 | 1.2211 | 0.62488 | 80 | 0.59627 | 0 | 4.2 | 3.6037 | 3.6037 |  | 1.05 | 4 | 0 | 4+4 | 8
85 | SS-35/10kv B.Kolodez | 2,5+2,5 | 0 | 1.1142 | 0.44779 | 45 | 0.6664 | 0 | 2.625 | 1.9586 | 1.9586 |  | 1.05 | 2.5 | 0 | 2,5+2,5 | 5
86 | SS-35/10kv B.Ples | 2,5+2,5 | 0.015 | 0.92017 | 0.606 | 45 | 0.31417 | 0 | 2.625 | 2.3108 | 2.3108 |  | 1.05 | 2.5 | 0.015 | 2,5+2,5 | 5
87 | SS-35/10kv B.Troitsa | 6,3+6,3 | 0.259 | 4.0312 | 2.83 | 45 | 1.2012 | 0 | 6.615 | 5.4138 | 5.4138 |  | 1.05 | 6.3 | 0.259 | 6,3+6,3 | 12.6
88 | SS-35/10kv Belovskoe | 4+4 | 0.105 | 4.0504 | 1.21 | 80 | 2.8404 | 0 | 4.2 | 1.3596 | 1.3596 |  | 1.05 | 4 | 0.105 | 4+4 | 8
89 | SS-35/10kv Belyanka | 2,5+4 | 0.014 | 2.1088 | 1.3214 | 45 | 0.78738 | 0 | 2.625 | 1.8376 | 1.8376 |  | 1.05 | 2.5 | 0.014 | 2,5+4 | 6.5
90 | SS-35/10kv Bessonovka | 6,3+6,3 | 0.04 | 7.1231 | 0.918 | 120 | 6.2051 | 0 | 6.615 | 0.40991 | 0.40991 |  | 1.05 | 6.3 | 0.04 | 6,3+6,3 | 12.6
91 | SS-35/10kv B.Lubyanki | 2,5+1,6 | 0.01 | 1.2728 | 0.522 | 45 | 0.75081 | 0 | 1.68 | 0.92919 | 0.92919 |  | 1.05 | 1.6 | 0.01 | 2,5+1,6 | 4.1
92 | SS-35/10kv V.Mikhailovka | 4+4 | 0.04 | 2.8528 | 1.45 | 80 | 1.4028 | 0 | 4.2 | 2.7972 | 2.7972 |  | 1.05 | 4 | 0.04 | 4+4 | 8
93 | SS-35/10kv Varvarovka | 2,5+2,5 | 0.1219 | 2.1281 | 1.0795 | 120 | 1.0485 | 0 | 2.625 | 1.5765 | 1.5765 |  | 1.05 | 2.5 | 0.1219 | 2,5+2,5 | 5
94 | SS-35/10kv Vengerovka | 2,5+2,5 | 0.53 | 1.6346 | 0.4 | 120 | 1.2346 | 0 | 2.625 | 1.3904 | 1.3904 |  | 1.05 | 2.5 | 0.53 | 2,5+2,5 | 5
95 | SS-35/10kv Verkhopenye | 2,5+4 | 0 | 1.5831 | 1.0177 | 45 | 0.56548 | 0 | 2.625 | 2.0595 | 2.0595 |  | 1.05 | 2.5 | 0 | 2,5+4 | 6.5
96 | SS-35/10kv Viktoropol | 2,5+4 | 0.01 | 1.4141 | 0.95536 | 120 | 0.45875 | 0 | 2.625 | 2.1662 | 2.1662 |  | 1.05 | 2.5 | 0.01 | 2,5+4 | 6.5
97 | SS-35/10kv Vislaya Dubrava | 4+4 | 0 | 2.723 | 0.616 | 80 | 2.107 | 0 | 4.2 | 2.093 | 2.093 |  | 1.05 | 4 | 0 | 4+4 | 8
98 | SS-35/10kv Vladimirovka | 4+4 | 0 | 0.75426 | 0 |  | 0.75426 | 0 | 4.2 | 3.4457 | 3.4457 |  | 1.05 | 4 | 0 | 4+4 | 8
99 | SS-35/10kv Water storage | 4+6,3 | 0 | 2.1769 | 0.305 | 45 | 1.8719 | 0 | 4.2 | 2.3281 | 2.3281 |  | 1.05 | 2.5 | 0 | 4+6,3 | 10.3
100 | SS-35/6kv Vostochnaya | 6,3+6,3 | 0.027 | 4.5899 | 1.43 | 120 | 3.1599 | 0 | 6.615 | 3.4551 | 3.4551 |  | 1.05 | 4 | 0.027 | 6,3+6,3 | 12.6
101 | SS-35/10kv Vsesvyatka | 2,5+2,5 | 0.026 | 2.1017 | 0.99513 | 120 | 1.1066 | 0 | 2.625 | 1.5184 | 1.5184 |  | 1.05 | 2.5 | 0.026 | 2,5+2,5 | 5
102 | SS-35/10kv Glinnoe | 6,3+6,3 | 0 | 2.9111 | 1.4036 | 80 | 1.5075 | 0 | 6.615 | 5.1075 | 5.1075 |  | 1.05 | 2.5 | 0 | 6,3+6,3 | 12.3
103 | SS-35/10kv Golovchino | 2,5+2,5 | 0.037 | 2.9036 | 0.617 | 45 | 2.2866 | 0 | 2.625 | 0.33841 | 0.33841 |  | 1.05 | 2.5 | 0.037 | 2,5+2,5 | 5
104 | SS-35/10kv Gora-Podol | 2,5+4 | 0 | 1.5901 | 0.9085 | 45 | 0.68155 | 0 | 2.625 | 1.9434 | 1.9434 |  | 1.05 | 2.5 | 0 | 2,5+4 | 6.5
105 | SS-35/10kv Gorodishche | 4+4 | 0.025 | 3.6314 | 0 |  | 3.6314 | 0 | 4.2 | 0.56864 | 0.56864 |  | 1.05 | 4 | 0.025 | 4+4 | 8
106 | SS-35/10kv Dmitrievka | 4+4 | 0.4 | 1.711 | 0.78237 | 80 | 0.92865 | 0 | 4.2 | 3.2713 | 3.2713 |  | 1.05 | 4 | 0.4 | 4+4 | 8
107 | SS-35/10kv Dorogoshch | 4+4 | 0.084 | 2.8473 | 1.054 | 45 | 1.7933 | 0 | 4.2 | 2.4067 | 2.4067 |  | 1.05 | 4 | 0.084 | 4+4 | 8
108 | SS-35/10kv Dragunka | 2,5+2,5 | 0.01 | 0.98757 | 0.62999 | 80 | 0.35758 | 0 | 2.625 | 2.2674 | 2.2674 |  | 1.05 | 2.5 | 0.01 | 2,5+2,5 | 5
109 | SS-35/10kv Zhuravlevka | 2,5+4 | 0.22 | 1.4816 | 0.274 | 80 | 1.2076 | 0 | 2.625 | 1.4174 | 1.4174 |  | 1.05 | 2.5 | 0.22 | 2,5+4 | 6.5
110 | SS-35/6kv Zhuravliki | 10+10 | 0.3609 | 8.118 | 4.051 | 120 | 4.067 | 0 | 10.5 | 6.433 | 6.433 |  | 1.05 | 10 | 0.3609 | 10+10 | 20
111 | SS-35/10kv Zavidovka | 2,5+2,5 | 0.03 | 0.6984 | 0.42 | 80 | 0.2784 | 0 | 2.625 | 2.3466 | 2.3466 |  | 1.05 | 2.5 | 0.03 | 2,5+2,5 | 5
112 | SS-35/6kv Zapadnaya | 10+10+10 | 0.06 | 7.4233 | 1.707 | 120 | 5.7163 | 0 | 21 | 15.2837 | 15.2837 |  | 1.05 | 20 | 0.06 | 10+10+10 | 30
113 | SS-35/10kv Zozuli | 6,3+6,3 | 0.175 | 6.6964 | 3.88 | 80 | 2.8164 | 0 | 6.615 | 3.7986 | 3.7986 |  | 1.05 | 6.3 | 0.175 | 6,3+6,3 | 12.6
114 | SS-35/10kv Ivitsa | 2,5+2,5 | 1.444 | 2.6988 | 0.58603 | 80 | 2.1128 | 0 | 2.625 | 0.51223 | 0.51223 |  | 1.05 | 2.5 | 1.444 | 2,5+2,5 | 5
115 | SS-35/10kv Ilovka | 4+4 | 0.862 | 3.8729 | 2.056 | 45 | 1.8169 | 0 | 4.2 | 2.3831 | 2.3831 |  | 1.05 | 4 | 0.862 | 4+4 | 8
116 | SS-35/10kv Istobnoe | 4+2,5 | 0 | 1.3775 | 0.93935 | 120 | 0.43818 | 0 | 2.625 | 2.1868 | 2.1868 |  | 1.05 | 2.5 | 0 | 4+2,5 | 6.5
117 | SS-35/10kv Kazatskaya | 2,5+4 | 0 | 1.6735 | 0.87141 | 45 | 0.80207 | 0 | 2.625 | 1.8229 | 1.8229 |  | 1.05 | 2.5 | 0 | 2,5+4 | 6.5
118 | SS-35/10kv Kazinka | 4+4 | 0.015 | 2.5189 | 0.736 | 120 | 1.7829 | 0 | 4.2 | 2.4171 | 2.4171 |  | 1.05 | 4 | 0.015 | 4+4 | 8
119 | SS-35/10kv Kamyshevatoe | 2,5+2,5 | 0.09 | 1.1905 | 0.712 | 120 | 0.47855 | 0 | 2.625 | 2.1465 | 2.1465 |  | 1.05 | 2.5 | 0.09 | 2,5+2,5 | 5
120 | SS-35/10kv Kirovskaya | 6,3+6,3 | 0.065 | 3.5534 | 0.7035 | 120 | 2.8499 | 0 | 6.615 | 3.7651 | 3.7651 |  | 1.05 | 6.3 | 0.065 | 6,3+6,3 | 12.6
121 | SS-35/10kv Kotovo | 2,5+2,5 | 0 | 2.7802 | 1.648 | 20 | 1.1322 | 0 | 2.625 | 1.4928 | 1.4928 |  | 1.05 | 2.5 | 0 | 2,5+2,5 | 5
122 | SS-35/10kv Kochetovka | 2,5+4 | 0 | 0.90697 | 0.6286 | 45 | 0.27838 | 0 | 2.625 | 2.3466 | 2.3466 |  | 1.05 | 2.5 | 0 | 2,5+4 | 6.5
123 | SS-35/10kv Krasnoe | 4+2,5 | 0 | 1.2051 | 1.1395 | 80 | 0.065535 | 0 | 2.625 | 2.5595 | 2.5595 |  | 1.05 | 2.5 | 0 | 4+2,5 | 6.5
124 | SS-35/10kv Kretovo | 4+2,5 | 0.107 | 1.315 | 0.67818 | 120 | 0.63683 | 0 | 2.625 | 1.9882 | 1.9882 |  | 1.05 | 2.5 | 0.107 | 4+2,5 | 6.5
125 | SS-35/10kv Kurasovka | 4+4 | 0.03 | 3.0638 | 1.797 | 80 | 1.2668 | 0 | 4.2 | 2.9332 | 2.9332 |  | 1.05 | 4 | 0.03 | 4+4 | 8
126 | SS-35/6kv Lebedi | 4+5,6 | 0.09 | 4.7212 | 0.581 | 120 | 4.1402 | 0 | 4.2 | 0.059842 | 0.059842 |  | 1.05 | 4 | 0.09 | 4+5,6 | 9.6
127 | SS-35/6kv Ledovaya | 4+4 | 0 | 2.8986 | 1.321 | 80 | 1.5776 | 0 | 4.2 | 2.6224 | 2.6224 |  | 1.05 | 4 | 0 | 4+4 | 8
128 | SS-35/10kv Livenka | 4+4 | 0.985 | 5.0933 | 1.541 | 120 | 3.5523 | 0 | 4.2 | 0.6477 | 0.6477 |  | 1.05 | 4 | 0.985 | 4+4 | 8
129 | SS-35/10kv Lubyanoe | 2,5+2,5 | 0 | 0.89358 | 0.66672 | 80 | 0.22686 | 0 | 2.625 | 2.3981 | 2.3981 |  | 1.05 | 2.5 | 0 | 2,5+2,5 | 5
130 | SS-35/10kv M.Pristan | 6,3+6,3 | 0.7663 | 7.6457 | 1.81 | 45 | 5.8357 | 0 | 6.615 | 0.77931 | 0.77931 |  | 1.05 | 6.3 | 0.7663 | 6,3+6,3 | 12.6
131 | SS-35/10kv М.Troitsa | 2,5+2,5 | 0.02 | 0.69679 | 0.60716 | 80 | 0.089632 | 0 | 2.625 | 2.5354 | 2.5354 |  | 1.05 | 2.5 | 0.02 | 2,5+2,5 | 5
132 | SS-35/10kv Malinovka | 10+10 | 0.04 | 6.9676 | 1.357 | 120 | 5.6106 | 0 | 10.5 | 4.8894 | 4.8894 |  | 1.05 | 10 | 0.04 | 10+10 | 20
133 | SS-35/10kv Mandrovo | 2,5+2,5 | 0.01 | 1.5611 | 0.65565 | 80 | 0.90548 | 0 | 2.625 | 1.7195 | 1.7195 |  | 1.05 | 2.5 | 0.01 | 2,5+2,5 | 5
134 | SS-35/10kv Mukhouderovka | 2,5+2,5 | 0.031 | 1.4854 | 0.643 | 80 | 0.84235 | 0 | 2.625 | 1.7826 | 1.7826 |  | 1.05 | 2.5 | 0.031 | 2,5+2,5 | 5
135 | SS-35/10kv N.Alexandrovka | 2,5+2,5 | 0 | 1.2266 | 0.59315 | 120 | 0.63346 | 0 | 2.625 | 1.9915 | 1.9915 |  | 1.05 | 2.5 | 0 | 2,5+2,5 | 5
136 | SS-35/10kv N.Derevnya | 6,3+6,3 | 0.181 | 6.3741 | 2.78 | 120 | 3.5941 | 0 | 6.615 | 3.0209 | 3.0209 |  | 1.05 | 4 | 0.181 | 6,3+6,3 | 12.6
137 | SS-35/10kv N.Tavolzhanka | 6,3+6,3 | 0.3192 | 3.8008 | 0.842 | 45 | 2.9588 | 0 | 6.615 | 3.6562 | 3.6562 |  | 1.05 | 6,3 | 0.3192 | 6,3+6,3 | 12.6
138 | SS-35/10kv N.Ukolovo | 4+2,5 | 1.245 | 3.0253 | 0.57 | 80 | 2.4553 | 0 | 2.625 | 0.16973 | 0.16973 |  | 1.05 | 2,5 | 1.245 | 4+2,5 | 6.5
139 | SS-35/10kv N.Khutornoe | 2,5+4 | 0.015 | 0.3415 | 0.19 | 80 | 0.1515 | 0 | 2.625 | 2.4735 | 2.4735 |  | 1.05 | 2,5 | 0.015 | 2,5+4 | 6.5
140 | SS-35/10kv Neminushchee | 4+2,5 | 0.08 | 1.7144 | 0.65147 | 80 | 1.0629 | 0 | 2.625 | 1.5621 | 1.5621 |  | 1.05 | 1,6 | 0.08 | 4+2,5 | 6.5
141 | SS-35/10kv Nechaevka | 4+4 | 0.055 | 1.4396 | 0.451 | 120 | 0.98865 | 0 | 4.2 | 3.2114 | 3.2114 |  | 1.05 | 4 | 0.055 | 4+4 | 8
142 | SS-35/10kv Nikitovka | 2,5+2,5 | 0.168 | 2.1973 | 1.4354 | 80 | 0.76187 | 0 | 2.625 | 1.8631 | 1.8631 |  | 1.05 | 2,5 | 0.168 | 2,5+2,5 | 5
143 | SS-35/10kv Novenkoe | 4+4 | 0 | 2.4166 | 1.7332 | 80 | 0.68339 | 0 | 4.2 | 3.5166 | 3.5166 |  | 1.05 | 4 | 0 | 4+4 | 8
144 | SS-35/10kv Oktyabrskaya | 6,3+6,3 | 0.494 | 7.9267 | 0.872 | 80 | 7.0547 | 0 | 6.615 | -0.4397 | -0.4397 |  | 1.05 | 6,3 | 0.494 | 6,3+6,3 | 12.6
145 | SS-35/10kv Orlik | 4+4 | 0.012 | 2.3158 | 0.553 | 80 | 1.7628 | 0 | 4.2 | 2.4372 | 2.4372 |  | 1.05 | 4 | 0.012 | 4+4 | 8
146 | SS-35/10kv Podolkhi | 2,5+2,5 | 0.42 | 2.086 | 1.1225 | 45 | 0.96355 | 0 | 2.625 | 1.6615 | 1.6615 |  | 1.05 | 2,5 | 0.42 | 2,5+2,5 | 5
147 | SS-35/10kv Popovka | 6,3+4 | 1.03 | 2.2972 | 0.64636 | 80 | 1.6509 | 0 | 4.2 | 2.5491 | 2.5491 |  | 1.05 | 4 | 1.03 | 6,3+4 | 10.4
148 | SS-35/10kv Prelestnoe | 4+4 | 0.085 | 2.4834 | 0 |  | 2.4834 | 0 | 4.2 | 1.7166 | 1.7166 |  | 1.05 | 6,3 | 0.085 | 4+4 | 8
149 | SS-35/6kv Privokzalnaya | 6,3+6,3 | 0.04 | 5.8161 | 0 |  | 5.8161 | 0 | 6.615 | 0.79892 | 0.79892 |  | 1.05 | 6.3 | 0.04 | 6,3+6,3 | 12.6
150 | SS-35/10kv Prilepy | 2,5+2,5 | 0 | 0.65233 | 0.37638 | 80 | 0.27596 | 0 | 2.625 | 2.349 | 2.349 |  | 1.05 | 2.5 | 0 | 2,5+2,5 | 5
151 | SS-35/10kv Printsevka | 2,5+2,5 | 0.02 | 1.5807 | 0.352 | 120 | 1.2287 | 0 | 2.625 | 1.3963 | 1.3963 |  | 1.05 | 2.5 | 0.02 | 2,5+2,5 | 5
152 | SS-35/10kv Radkovka | 6,3+6,3 | 0.09 | 2.8953 | 0.164 | 45 | 2.7313 | 0 | 6.615 | 3.8837 | 3.8837 |  | 1.05 | 4 | 0.09 | 6,3+6,3 | 12.6
153 | SS-35/10kv Razdornoe | 2,5+2,5 | 0 | 1.4347 | 0.662 | 80 | 0.7727 | 0 | 2.625 | 1.8523 | 1.8523 |  | 1.05 | 2.5 | 0 | 2,5+2,5 | 5
154 | SS-35/10kv Repyakhovka | 2,5+2,5 | 0 | 1.6386 | 0.88491 | 80 | 0.75368 | 0 | 2.625 | 1.8713 | 1.8713 |  | 1.05 | 2.5 | 0 | 2,5+2,5 | 5
155 | SS-35/10kv Rzhevka | 10+10 | 0.135 | 7.5416 | 2.53 | 45 | 5.0116 | 0 | 10.5 | 5.4884 | 5.4884 |  | 1.05 | 6.3 | 0.135 | 10+10 | 20
156 | SS-35/10kv Rovenki | 4+4 | 0 | 3.4807 | 1.7393 | 120 | 1.7414 | 0 | 4.2 | 2.4586 | 2.4586 |  | 1.05 | 4 | 0 | 4+4 | 8
157 | SS-35/10kv Rogovatoe | 2,5+2,5 | 1.433 | 3.1294 | 0 |  | 3.1294 | 0 | 2.625 | -0.50438 | -0.50438 |  | 1.05 | 2.5 | 1.433 | 2,5+2,5 | 5
158 | SS-35/10kv Saprykino | 2,5+2,5 | 0.015 | 0.44433 | 0.22751 | 120 | 0.21681 | 0 | 2.625 | 2.4082 | 2.4082 |  | 1.05 | 2.5 | 0.015 | 2,5+2,5 | 5
159 | SS-35/6kv Severnaya | 6,3+6,3 | 0.0338 | 6.5759 | 4.8049 | 120 | 1.7709 | 0 | 6.615 | 4.8441 | 4.8441 |  | 1.05 | 6.3 | 0.0338 | 6,3+6,3 | 12.6
160 | SS-35/10kv Setishche | 2,5+2,5 | 0.035 | 2.0536 | 1.0621 | 80 | 0.9915 | 0 | 2.625 | 1.6335 | 1.6335 |  | 1.05 | 2.5 | 0.035 | 2,5+2,5 | 5
161 | SS-35/10kv Slonovka | 4+4 | 0.85 | 3.4737 | 1.1306 | 120 | 2.3431 | 0 | 4.2 | 1.8569 | 1.8569 |  | 1.05 | 4 | 0.85 | 4+4 | 8
162 | SS-35/6kv St.Oskol -2 | 16+16 | 0.209 | 12.8701 | 1.21 | 80 | 11.6601 | 0 | 16.8 | 5.1399 | 5.1399 |  | 1.05 | 16 | 0.209 | 16+16 | 32
163 | SS-35/10kv Starikovo | 4+4 | 0 | 1.6059 | 1.3453 | 45 | 0.26059 | 0 | 4.2 | 3.9394 | 3.9394 |  | 1.05 | 2.5 | 0 | 4+4 | 8
164 | SS-35/10kv Tavrovo | 10+10 | 1.157 | 9.8462 | 0.531 | 45 | 9.3152 | 0 | 10.5 | 1.1848 | 1.1848 |  | 1.05 | 10 | 1.157 | 10+10 | 20
165 | SS-35/10kv Terebrino | 2,5+2,5 | 0 | 1.2845 | 0.44978 | 80 | 0.83472 | 0 | 2.625 | 1.7903 | 1.7903 |  | 1.05 | 2.5 | 0 | 2,5+2,5 | 5
166 | SS-35/10kv Urazovo | 6,3+6,3 | 0.13 | 5.1433 | 1.39 | 120 | 3.7533 | 0 | 6.615 | 2.8617 | 2.8617 |  | 1.05 | 6.3 | 0.13 | 6,3+6,3 | 12.6
167 | SS-35/10kv Utochka | 1,6+2,5 | 0 | 0.73424 | 0.47242 | 80 | 0.26182 | 0 | 1.68 | 1.4182 | 1.4182 |  | 1.05 | 1.6 | 0 | 1,6+2,5 | 4.1
168 | SS-35/6kv Fedoseevka | 4+4 | 0.07 | 2.3351 | 0 |  | 2.3351 | 0 | 4.2 | 1.8649 | 1.8649 |  | 1.05 | 4 | 0.07 | 4+4 | 8
169 | SS-35/10kv Foshchevatvo | 1,6+2,5 | 0.01 | 1.0715 | 0.78681 | 45 | 0.28473 | 0 | 1.68 | 1.3953 | 1.3953 |  | 1.05 | 1.6 | 0.039 | 1,6+2,5 | 4.1
170 | SS-35/10kv Kholodnoe | 4+4 | 0.025 | 1.8092 | 0 |  | 1.8092 | 0 | 4.2 | 2.3908 | 2.3908 |  | 1.05 | 2.5 | 0.025 | 4+4 | 8
171 | SS-35/6kv Chernyansky sugar plant | 7,5+6,3 | 0 | 1.9642 | 1.3513 | 20 | 0.61293 | 0 | 6.615 | 6.0021 | 6.0021 |  | 1.05 | 6.3 | 0 | 7,5+6,3 | 13.8
172 | SS-35/10kv Shatalovka | 6,3+6,3 | 0.1 | 2.1637 | 0 |  | 2.1637 | 0 | 6.615 | 4.4513 | 4.4513 |  | 1.05 | 6.3 | 0.1 | 6,3+6,3 | 12.6
173 | SS-35/10kv Shakhovka | 2,5+2,5 | 0.052 | 1.7529 | 0.79066 | 80 | 0.96221 | 0 | 2.625 | 1.6628 | 1.6628 |  | 1.05 | 2.5 | 0.052 | 2,5+2,5 | 5
174 | SS-35/10kv Shishino | 4+6,3 | 0.2 | 3.7723 | 1.03 | 80 | 2.7423 | 0 | 4.2 | 1.4577 | 1.4577 |  | 1.05 | 2.5 | 0.2 | 4+6,3 | 10.3
175 | SS-35/10kv Yablonovo | 4+4 | 0 | 1.8006 | 1.1284 | 80 | 0.6722 | 0 | 4.2 | 3.5278 | 3.5278 |  | 1.05 | 4 | 0 | 4+4 | 8
176 | SS-35/10kv Yarskoe | 2,5+2,5 | 0 | 0.56896 | 0.14648 | 80 | 0.42248 | 0 | 2.625 | 2.2025 | 2.2025 |  | 1.05 | 2.5 | 0 | 2,5+2,5 | 5
| TOTAL: | 3186.9 | 64.7046 | #VALUE! | 453.9275 |  | #VALUE! | [9 empty] | 3049.2
| deficit | [9 empty] | #REF!
| proficit | [9 empty] | 833.0636 | [5 empty] | 3186.9

## Итоговая
No. | Object of main substation, voltage class | Current deficit | [10 empty] | Note | No. | Object of main substation, voltage class | Expected deficit/proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sуst. Including their number, pcs/ MVA | P | Q | Summary total capacity of central substation following the results of measurements of load maximal Sмах | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit/proficit of Main Substation, MVA |  |  |  |  | Installed power capacity of transformers Sуst. Including their number, pcs/ MVA | Additional capacity according to provided technical specifications at TS, MVA | Expected load of Main substation, MVA | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load calculated in the n-1 mode, MVA | Deficit/proficit of Main Substation, MVA
[5 empty] | MVA | MVA | Min | [11 empty] | MVA | Min
1 | 2 | 4 |  |  | 5 | 6 | 7 | 8 | 9 | 10 | 11 |  | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
One-transformer substations | [13 empty] | 1: One-transformer substations
1 | SS-110/35/10kv D.Polyana | 6.3 | 1523 | 679 | 1.6675 | 1.457 | 45 | 1.457 | 0 | 1.457 | -0.2105 | -0.57942 |  | 1 | SS-110/35/10kv D.Polyana | 6.3 | 0 | 1.6675 | 1.457 | 45 | 0.2105 | 0 | 1.457 | -0.2105 | #VALUE!
| Sн. MV, МVА | 6.3 | 513 | 301 | 0.59479 | 0.958 |  | 0.958 | 0 | 0.958 | 0.36321 |  |  |  | Sн. MV, МVА | 6.3 | 0 | 0.59479 | 0.958 | 0 | -0.36321 | 0 | 0.958 | 0.36321
| Sн. LV, МVА | 6.3 | 1010 | 378 | 1.0784 | 0.499 |  | 0.499 | 0 | 0.499 | -0.57942 |  |  |  | Sн. LV, МVА | 6.3 | 0 | 1.0784 | 0.499 | 0 | 0.57942 | 0 | 0.499 | -0.57942
2 | SS-110/35/10kv Konshino | 6.3 | 375 | 154 | 0.40539 | 0.39 | 20 | 0.39 | 0 | 0.39 | -0.01539 | -0.01539 |  | 2 | SS-110/35/10kv Konshino | 6.3 | 0 | 0.40539 | 0.39 | 20 | 0.01539 | 0 | 0.39 | -0.01539 | #VALUE!
| Sн. MV, МVА | 6.3 |  |  | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | Sн. MV, МVА | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Sн. LV, МVА | 6.3 | 375 | 154 | 0.40539 | 0.39 |  | 0.39 | 0 | 0.39 | -0.01539 |  |  |  | Sн. LV, МVА | 6.3 | 0 | 0.40539 | 0.39 | 0 | 0.01539 | 0 | 0.39 | -0.01539
3 | SS-110/35/10kv Orositelnaya | 16 | 11884 | 2898 | 12.2322 | 11.607 | 120 | 11.607 | 0 | 11.607 | -0.62525 | -0.90525 |  | 3 | SS-110/35/10kv Orositelnaya | 16 | 0 | 12.2322 | 11.607 | 120 | 0.62525 | 0 | 11.607 | -0.62525 | -0.90525
| Sн. MV, МVА | 16 | 9059 | 2898 | 9.5113 | 8.606 |  | 8.606 | 0 | 8.606 | -0.90525 |  |  |  | Sн. MV, МVА | 16 | 0 | 9.5113 | 8.606 | 0 | 0.90525 | 0 | 8.606 | -0.90525
| Sн. LV, МVА | 16 | 2825 |  | 2.825 | 3.001 |  | 3.001 | 0 | 3.001 | 0.176 |  |  |  | Sн. LV, МVА | 16 | 0 | 2.825 | 3.001 | 0 | -0.176 | 0 | 3.001 | 0.176
4 | SS-110/35/6kv Pishcheprom | 25 | 6036 | 1850 | 6.3131 | 6.679 | 120 | 6.679 | 0 | 6.679 | 0.36586 | -0.24769 |  | 4 | SS-110/35/6kv Pishcheprom | 25 | 1.267 | 7.5801 | 6.679 | 120 | 0.90114 | 0 | 6.679 | -0.90114 | -0.90114
| Sн. MV, МVА | 12.5 | 2171 | 662 | 2.2697 | 2.022 |  | 2.022 | 0 | 2.022 | -0.24769 |  |  |  | Sн. MV, МVА | 12.5 | 0 | 2.2697 | 2.022 | 0 | 0.24769 | 0 | 2.022 | -0.24769
| Sн. LV, МVА | 12.5 | 3865 | 1188 | 4.0435 | 4.657 |  | 4.657 | 0 | 4.657 | 0.61354 |  |  |  | Sн. LV, МVА | 12.5 | 1.267 | 5.3105 | 4.657 | 0 | 0.65346 | 0 | 4.657 | -0.65346
5 | SS-110/35/10kv Rovenki | 16 | 2453 | 976 | 2.64 | 3.44 | 120 | 3.44 | 0 | 3.44 | 0.79996 | 0.79996 |  | 5 | SS-110/35/10kv Rovenki | 16 | 0.709 | 3.349 | 3.44 | 120 | -0.090965 | 0 | 3.44 | 0.090965 | 0.79996
| Sн. MV, МVА | 16 | 2 | 34 | 0.034059 | 4 |  | 4 | 0 | 4 | 3.9659 |  |  |  | Sн. MV, МVА | 16 | 0.614 | 0.64806 | 4 | 0 | -3.3519 | 0 | 4 | 3.3519
| Sн. LV, МVА | 16 | 2451 | 942 | 2.6258 | 3.44 |  | 3.44 | 0 | 3.44 | 0.81421 |  |  |  | Sн. LV, МVА | 16 | 0.095 | 2.7208 | 3.44 | 0 | -0.71921 | 0 | 3.44 | 0.71921
6 | SS-110/35/10kv Serebryanka | 10 | 1181 | 534 | 1.2961 | 1.78 | 45 | 1.78 | 0 | 1.78 | 0.48388 | 0 |  | 6 | SS-110/35/10kv Serebryanka | 10 | 0 | 1.2961 | 1.78 | 45 | -0.48388 | 0 | 1.78 | 0.48388 | 0
| Sн. MV, МVА | 10 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | Sн. MV, МVА | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Sн. LV, MVА | 10 | 1181 | 534 | 1.2961 | 1.78 |  | 1.78 | 0 | 1.78 | 0.48388 |  |  |  | Sн. LV, MVА | 10 | 0 | 1.2961 | 1.78 | 0 | -0.48388 | 0 | 1.78 | 0.48388
7 | SS-35/10kv Afanasyevka | 1.6 | 868 | 280 | 0.91204 | 0.6464 | 45 | 0.6464 | 0 | 0.6464 | -0.26564 | -0.26564 |  | 7 | SS-35/10kv Afanasyevka | 1.6 | 0 | 0.91204 | 0.6464 | 45 | 0.26564 | 0 | 0.6464 | -0.26564 | -0.26564
8 | SS-35/10kv Borisovka | 1.6 | 576 | 192 | 0.60716 | 0.6835 | 45 | 0.6835 | 0 | 0.6835 | 0.076343 | 0.076343 |  | 8 | SS-35/10kv Borisovka | 1.6 | 0 | 0.60716 | 0.6835 | 45 | -0.076343 | 0 | 0.6835 | 0.076343 | 0.076343
9 | SS-35/10kv Borisy | 1.6 | 432 | 234 | 0.4913 | 0 | 20 | 0 | 0 | 0 | -0.4913 | -0.4913 |  | 9 | SS-35/10kv Borisy | 1.6 | 2.083 | 2.5743 | 0 | 20 | 2.5743 | 0 | 0 | -2.5743 | -0.8813
10 | SS-35/10kv Gostishchevo | 4 | 3792 | 1440 | 4.0562 | 2.64 | 80 | 2.64 | 0 | 2.64 | -1.4162 | -1.4162 |  | 10 | SS-35/10kv Gostishchevo | 4 | 0.28 | 4.3362 | 2.64 | 80 | 1.6962 | 0 | 2.64 | -1.6962 | -1.4162
11 | SS-35/10kv Gruzskoe | 1.6 | 606 | 264 | 0.66101 | 1.05 | 80 | 1.05 | 0 | 1.05 | 0.38899 | 0.38899 |  | 11 | SS-35/10kv Gruzskoe | 1.6 | 0 | 0.66101 | 1.05 | 80 | -0.38899 | 0 | 1.05 | 0.38899 | 0.38899
12 | SS-35/10kv Zemsnaryad | 1.6 | 14 | 14 | 0.019799 | 0 |  | 0 | 0 | 0 | -0.019799 | -0.019799 |  | 12 | SS-35/10kv Zemsnaryad | 1.6 | 0.185 | 0.2048 | 0 | 0 | 0.2048 | 0 | 0 | -0.2048 | -0.019799
13 | SS-35/10kv Kazachya Lisitsa | 2.5 | 360 | 112 | 0.37702 | 0 |  | 0 | 0 | 0 | -0.37702 | -0.37702 |  | 13 | SS-35/10kv Kazachya Lisitsa | 2.5 | 0 | 0.37702 | 0 | 0 | 0.37702 | 0 | 0 | -0.37702 | -0.37702
14 | SS-35/10kv Kamyzino | 2.5 | 992 | 392 | 1.0666 | 0.541 | 45 | 0.541 | 0 | 0.541 | -0.52564 | -0.52564 |  | 14 | SS-35/10kv Kamyzino | 2.5 | 0 | 1.0666 | 0.541 | 45 | 0.52564 | 0 | 0.541 | -0.52564 | -0.52564
15 | SS-35/10kv Koloskovo | 2.5 | 2000 | 624 | 2.0951 | 1.6626 | 45 | 1.6626 | 0 | 1.6626 | -0.43248 | -0.43248 |  | 15 | SS-35/10kv Koloskovo | 2.5 | 0.025 | 2.1201 | 1.6626 | 45 | 0.45748 | 0 | 1.6626 | -0.45748 | -0.43248
16 | SS-35/10jkv Kryukovo | 2.5 | 1584 | 492 | 1.6587 | 1.55 | 45 | 1.55 | 0 | 1.55 | -0.10865 | -0.10865 |  | 16 | SS-35/10jkv Kryukovo | 2.5 | 0 | 1.6587 | 1.55 | 45 | 0.10865 | 0 | 1.55 | -0.10865 | -0.10865
17 | SS-35/10kv Kushchino | 1.6 | 384 | 144 | 0.41011 | 0.4101 | 80 | 0.4101 | 0 | 0.4101 | -1.218e-05 | -1.218e-05 |  | 17 | SS-35/10kv Kushchino | 1.6 | 0 | 0.41011 | 0.4101 | 80 | 1.218e-05 | 0 | 0.4101 | -1.218e-05 | -1.218e-05
18 | SS-35/10kv Lopukhinka | 2.5 | 384 | 160 | 0.416 | 0.407 | 20 | 0.407 | 0 | 0.407 | -0.009 | -0.009 |  | 18 | SS-35/10kv Lopukhinka | 2.5 | 0 | 0.416 | 0.407 | 20 | 0.009 | 0 | 0.407 | -0.009 | -0.009
19 | SS-35/10kv Malakeevo | 2.5 | 1296 | 648 | 1.449 | 1.38 | 120 | 1.38 | 0 | 1.38 | -0.068972 | -0.068972 |  | 19 | SS-35/10kv Malakeevo | 2.5 | 0.014 | 1.463 | 1.38 | 120 | 0.082972 | 0 | 1.38 | -0.082972 | -0.068972
20 | SS-35/10kv Murom | 2.5 | 1336 | 432 | 1.4041 | 1.54 | 45 | 1.54 | 0 | 1.54 | 0.13589 | 0.13589 |  | 20 | SS-35/10kv Murom | 2.5 | 0 | 1.4041 | 1.54 | 45 | -0.13589 | 0 | 1.54 | 0.13589 | 0.087192
21 | SS-35/10kv Nikolaevka | 2.5 | 664 | 288 | 0.72377 | 0.6647 | 45 | 0.6647 | 0 | 0.6647 | -0.059068 | -0.059068 |  | 21 | SS-35/10kv Nikolaevka | 2.5 | 0 | 0.72377 | 0.6647 | 45 | 0.059068 | 0 | 0.6647 | -0.059068 | -0.059068
22 | SS-35/10kv Nikolskoe | 4 | 1776 | 396 | 1.8196 | 0.78 | 120 | 0.78 | 0 | 0.78 | -1.0396 | -1.0396 |  | 22 | SS-35/10kv Nikolskoe | 4 | 0.2421 | 2.0617 | 0.78 | 120 | 1.2817 | 0 | 0.78 | -1.2817 | -1.0396
23 | SS-35/10kv Pokrovka | 4 | 708 | 300 | 0.76894 | 0.722 | 45 | 0.722 | 0 | 0.722 | -0.046937 | -0.046937 |  | 23 | SS-35/10kv Pokrovka | 4 | 0.013 | 0.78194 | 0.722 | 45 | 0.059937 | 0 | 0.722 | -0.059937 | -0.21494
24 | SS-35/10kv Pyatnitskoe | 4 | 2441 | 768 | 2.559 | 1.84 | 80 | 1.84 | 0 | 1.84 | -0.71897 | -0.71897 |  | 24 | SS-35/10kv Pyatnitskoe | 4 | 0.035 | 2.594 | 1.84 | 80 | 0.75397 | 0 | 1.84 | -0.75397 | -0.71897
25 | SS-35/10kv Sugar plant Ivnya | 2.5 | 94 | 151 | 0.17787 | 1.676 | 80 | 1.676 | 0 | 1.676 | 1.4981 | 1.4981 |  | 25 | SS-35/10kv Sugar plant Ivnya | 2.5 | 0 | 0.17787 | 1.676 | 80 | -1.4981 | 0 | 1.676 | 1.4981 | 1.4981
26 | SS-35/10kv Svistovka | 2.5 | 616 | 304 | 0.68693 | 0.6872 | 45 | 0.6872 | 0 | 0.6872 | 0.0002706 | 0.0002706 |  | 26 | SS-35/10kv Svistovka | 2.5 | 0.035 | 0.72193 | 0.6872 | 45 | 0.034729 | 0 | 0.6872 | -0.034729 | 0.0002706
27 | SS-35/10kv sovkhoz "Urazovsky" | 2.5 | 688 | 244 | 0.72999 | 0.7238 | 120 | 0.7238 | 0 | 0.7238 | -0.0061863 | -0.0061863 |  | 27 | SS-35/10kv sovkhoz "Urazovsky" | 2.5 | 0 | 0.72999 | 0.7238 | 120 | 0.0061863 | 0 | 0.7238 | -0.0061863 | -0.0061863
28 | SS-35/10kv Kharkovskaya | 2.5 | 660 | 304 | 0.72665 | 0.6797 | 120 | 0.6797 | 0 | 0.6797 | -0.046947 | -0.046947 |  | 28 | SS-35/10kv Kharkovskaya | 2.5 | 0 | 0.72665 | 0.6797 | 120 | 0.046947 | 0 | 0.6797 | -0.046947 | -0.046947
29 | SS-35/10kv Tserkovnaya | 2.5 | 1112 | 288 | 1.1487 | 1 | 80 | 1 | 0 | 1 | -0.14869 | -0.14869 |  | 29 | SS-35/10kv Tserkovnaya | 2.5 | 0 | 1.1487 | 1 | 80 | 0.14869 | 0 | 1 | -0.14869 | -0.14869
Two- and more transformer substations | [13 empty] | 1: Two- and more transformer substations
30 | SS-110/6kv Automobile maintenance plant | 16+16 | 13361 | 7836 | 15.4893 | 3.561 | 45 | 11.9283 | 0 | 16.8 | 4.8717 | 4.8717 |  | 30 | SS-110/6kv Automobile maintenance plant | 16+16 | 0.952 | 16.4413 | 3.561 | 45 | 12.8803 | 0 | 16.8 | 3.9197 | #VALUE!
31 | SS-110/35/10kv Aydar | 16+10 | 9152 | 3513 | 9.8031 | 8.95 | 120 | 0.85307 | 0 | 10.5 | 9.6469 | 9.6416 |  | 31 | SS-110/35/10kv Aydar | 16+10 | 0.03 | 9.8331 | 8.95 | 120 | 0.88307 | 0 | 10.5 | 9.6169 | 9.6416
| Sн. MV, МVА | 16+10 | 7582 | 2985 | 8.1484 | 7.29 |  | 0.85843 | 0 | 10.5 | 9.6416 |  |  |  | Sн. MV, МVА | 16+10 | 0 | 8.1484 | 7.29 | 0 | 0.85843 | 0 | 10.5 | 9.6416
| Sн. LV, МVА | 16+10 | 1570 | 528 | 1.6564 | 1.66 |  | -0.003593 | 0 | 10.5 | 10.5036 |  |  |  | Sн. LV, МVА | 16+10 | 0.03 | 1.6864 | 1.66 | 0 | 0.026407 | 0 | 10.5 | 10.4736
32 | SS-110/35/10kv Alexandrovka | 16+16 | 12411 | 4290 | 13.1315 | 8.37 | 80 | 4.7615 | 0 | 16.8 | 12.0385 | 12.0385 |  | 32 | SS-110/35/10kv Alexandrovka | 16+16 | 12.3214 | 25.4529 | 8.37 | 80 | 17.0829 | 0 | 16.8 | -0.28293 | 11.4135
| Sн. MV, МVА | 16+16 | 6573 | 2264 | 6.952 | 6.697 |  | 0.25498 | 0 | 16.8 | 16.545 |  |  |  | Sн. MV, МVА | 16+16 | 0 | 6.952 | 6.697 | 0 | 0.25498 | 0 | 16.8 | 16.545
| Sн. LV, МVА | 16+16 | 5838 | 2026 | 6.1796 | 1.673 |  | 4.5066 | 0 | 16.8 | 12.2934 |  |  |  | Sн. LV, МVА | 16+16 | 12.3214 | 18.501 | 1.673 | 0 | 16.828 | 0 | 16.8 | -0.027957
33 | SS-110/35/10kv Alexeevka | 25+25+25 | 39765 | 17571 | 43.4741 | 5.322 | 120 | 38.1521 | 0 | 52.5 | 14.3479 | 14.3479 |  | 33 | SS-110/35/10kv Alexeevka | 25+25+25 | 0 | 43.4741 | 5.322 | 120 | 38.1521 | 0 | 52.5 | 14.3479 | 14.3479
| Sн. MV, МVА | 25+25+25 | 16965 | 8691 | 19.0616 | 3.102 |  | 15.9596 | 0 | 52.5 | 36.5404 |  |  |  | Sн. MV, МVА | 25+25+25 | 0 | 19.0616 | 3.102 | 0 | 15.9596 | 0 | 52.5 | 36.5404
| Sн. LV, МVА | 25+25+25 | 22800 | 8880 | 24.4682 | 2.22 |  | 22.2482 | 0 | 52.5 | 30.2518 |  |  |  | Sн. LV, МVА | 25+25+25 | 1.3985 | 25.8667 | 2.22 | 0 | 23.6467 | 0 | 52.5 | 28.8533
34 | SS-110/35/10kv Arkhangelskoe | 10+16 | 10006 | 3960 | 10.7611 | 8.87 | 45 | 1.8911 | 0 | 10.5 | 8.6089 | 8.6089 |  | 34 | SS-110/35/10kv Arkhangelskoe | 10+16 | 0.015 | 10.7761 | 8.87 | 45 | 1.9061 | 0 | 10.5 | 8.5939 | 8.6089
| Sн. MV, МVА | 10+16 | 9416 | 3776 | 10.1449 | 8.867 |  | 1.2779 | 0 | 10.5 | 9.2221 |  |  |  | Sн. MV, МVА | 10+16 | 0 | 10.1449 | 8.867 | 0 | 1.2779 | 0 | 10.5 | 9.2221
| Sн. LV, МVА | 10+16 | 590 | 184 | 0.61803 | 0 |  | 0.61803 | 0 | 10.5 | 9.882 |  |  |  | Sн. LV, МVА | 10+16 | 0.015 | 0.63303 | 0 | 0 | 0.63303 | 0 | 10.5 | 9.867
35 | SS-110/6kv Belgorod-1 | 40+48 | 42786 | 13076 | 44.7395 | 0 | 120 | 44.7395 | 0 | 42 | -2.7395 | -2.7395 |  | 35 | SS-110/6kv Belgorod-1 | 40+48 | 0.747 | 45.4865 | 0 | 120 | 45.4865 | 0 | 42 | -3.4865 | #VALUE!
36 | SS-110/35/10kv Borisovka | 16+16 | 11354 | 4570 | 12.2392 | 11.433 | 120 | 0.80621 | 0 | 16.8 | 15.9938 | 4.8462 |  | 36 | SS-110/35/10kv Borisovka | 16+16 | 0 | 12.2392 | 11.433 | 120 | 0.80621 | 0 | 16.8 | 15.9938 | 4.8182
| Sн. MV, МVА | 16+8 | 4826 | 2482 | 5.4268 | 8.133 |  | -2.7062 | 0 | 8.4 | 11.1062 |  |  |  | Sн. MV, МVА | 16+8 | 0 | 5.4268 | 8.133 | 0 | -2.7062 | 0 | 8.4 | 11.1062
| Sн. LV, МVА | 16+8 | 6528 | 2088 | 6.8538 | 3.3 |  | 3.5538 | 0 | 8.4 | 4.8462 |  |  |  | Sн. LV, МVА | 16+8 | 0.038 | 6.8918 | 3.3 | 0 | 3.5918 | 0 | 8.4 | 4.8082
37 | SS-110/35/10kv V.Pokrovka | 10+10 | 9651 | 3834 | 10.3847 | 11.5 | 120 | -1.1153 | 0 | 10.5 | 11.6153 | 9.4887 |  | 37 | SS-110/35/10kv V.Pokrovka | 10+10 | 0 | 10.3847 | 11.5 | 120 | -1.1153 | 0 | 10.5 | 11.6153 | 9.4887
| Sн. MV, МVА | 10+10 | 8148 | 3354 | 8.8113 | 7.8 |  | 1.0113 | 0 | 10.5 | 9.4887 |  |  |  | Sн. MV, МVА | 10+10 | 0 | 8.8113 | 7.8 | 0 | 1.0113 | 0 | 10.5 | 9.4887
| Sн. LV, МVА | 10+10 | 1503 | 480 | 1.5778 | 3.7 |  | -2.1222 | 0 | 10.5 | 12.6222 |  |  |  | Sн. LV, МVА | 10+10 | 0 | 1.5778 | 3.7 | 0 | -2.1222 | 0 | 10.5 | 12.6222
38 | SS-110/35/10kv Veydelevka | 10+10 | 9151 | 3160 | 9.6812 | 8.83 | 120 | 0.85124 | 0 | 10.5 | 9.6488 | 9.1219 |  | 38 | SS-110/35/10kv Veydelevka | 10+10 | 0.015 | 9.6962 | 8.83 | 120 | 0.86624 | 0 | 10.5 | 9.6338 | 9.1219
| Sн. MV, МVА | 10+10 | 4999 | 1858 | 5.3331 | 3.955 |  | 1.3781 | 0 | 10.5 | 9.1219 |  |  |  | Sн. MV, МVА | 10+10 | 0 | 5.3331 | 3.955 | 0 | 1.3781 | 0 | 10.5 | 9.1219
| Sн. LV, МVА | 10+10 | 4152 | 1302 | 4.3514 | 4.875 |  | -0.52364 | 0 | 10.5 | 11.0236 |  |  |  | Sн. LV, МVА | 10+10 | 0.015 | 4.3664 | 4.875 | 0 | -0.50864 | 0 | 10.5 | 11.0086
39 | SS-110/6kv Vitamin plant | 25+25 | 13429 | 6832 | 15.067 | 1.46 | 45 | 13.607 | 0 | 26.25 | 12.643 | 12.643 |  | 39 | SS-110/6kv Vitamin plant | 25+25 | 3.656 | 18.723 | 1.46 | 45 | 17.263 | 0 | 26.25 | 8.987 | #VALUE!
40 | SS-110/35/10kv Volokonovka | 25+25 | 18812 | 6807 | 20.0057 | 10.651 | 120 | 9.3547 | 0 | 26.25 | 16.8953 | 16.8953 |  | 40 | SS-110/35/10kv Volokonovka | 25+25 | 0.223 | 20.2287 | 10.651 | 120 | 9.5777 | 0 | 26.25 | 16.6723 | #VALUE!
| Sн. MV, МVА | 25+25 | 10517 | 4038 | 11.2656 | 8.576 |  | 2.6896 | 0 | 26.25 | 23.5604 |  |  |  | Sн. MV, МVА | 25+25 | 0 | 11.2656 | 8.576 | 0 | 2.6896 | 0 | 26.25 | 23.5604
| Sн. LV, МVА | 25+25 | 8295 | 2769 | 8.745 | 2.075 |  | 6.67 | 0 | 26.25 | 19.58 |  |  |  | Sн. LV, МVА | 25+25 | 0.223 | 8.968 | 2.075 | 0 | 6.893 | 0 | 26.25 | 19.357
41 | SS-110/35/6kv Vostochnaya | 25+25 | 37165 | 16321 | 40.5908 | 25.07 | 120 | 15.5208 | 0 | 26.25 | 10.7292 | 6.2914 |  | 41 | SS-110/35/6kv Vostochnaya | 25+25 | 1.8005 | 42.3913 | 25.07 | 120 | 17.3213 | 0 | 26.25 | 8.9287 | #VALUE!
| Sн. MV, МVА | 25+25 | 16029 | 5536 | 16.9581 | 21.3 |  | -4.3419 | 0 | 26.25 | 30.5919 |  |  |  | Sн. MV, МVА | 25+25 | 0 | 16.9581 | 21.3 | 0 | -4.3419 | 0 | 26.25 | 30.5919
| Sн. LV, МVА | 25+25 | 21136 | 10785 | 23.7286 | 3.77 |  | 19.9586 | 0 | 26.25 | 6.2914 |  |  |  | Sн. LV, МVА | 25+25 | 1.8005 | 25.5291 | 3.77 | 0 | 21.7591 | 0 | 26.25 | 4.4909
42 | SS-110/10/6kv Golofeevka | 25+25 | 2404 | 964 | 2.5901 | 0 |  | 2.5901 | 0 | 26.25 | 23.6599 | 10.5349 |  | 42 | SS-110/10/6kv Golofeevka | 25+25 | 0.25 | 2.8401 | 0 | 0 | 2.8401 | 0 | 26.25 | 23.4099 | #VALUE!
| Sн. MV, МVА | 12,5+12,5 | 0 | 0 | 0 | 0 |  | 0 | 0 | 13.125 | 13.125 |  |  |  | Sн. MV, МVА | 12,5+12,5 | 0 | 0 | 0 | 0 | 0 | 0 | 13.125 | 13.125
| Sн. LV, МVА | 12,5+12,5 | 2404 | 964 | 2.5901 | 0 |  | 2.5901 | 0 | 13.125 | 10.5349 |  |  |  | Sн. LV, МVА | 12,5+12,5 | 0.25 | 2.8401 | 0 | 0 | 2.8401 | 0 | 13.125 | 10.2849
43 | SS-110/10kv Gotnya | 16+16 | 8388 | 3608 | 9.1311 | 6.43 | 120 | 2.7011 | 0 | 16.8 | 14.0989 | 14.0989 |  | 43 | SS-110/10kv Gotnya | 16+16 | 0.063 | 9.1941 | 6.43 | 120 | 2.7641 | 0 | 16.8 | 14.0359 | #VALUE!
44 | SS-110/35/10kv Grayvoron | 16+16 | 13281 | 5063 | 14.2133 | 13.953 | 80 | 0.26034 | 0 | 16.8 | 16.5397 | 14.4501 |  | 44 | SS-110/35/10kv Grayvoron | 16+16 | 0.03 | 14.2433 | 13.953 | 80 | 0.29034 | 0 | 16.8 | 16.5097 | 14.4201
| Sн. MV, МVА | 16+16 | 8161 | 3347 | 8.8207 | 10.903 |  | -2.0823 | 0 | 16.8 | 18.8823 |  |  |  | Sн. MV, МVА | 16+16 | 0 | 8.8207 | 10.903 | 0 | -2.0823 | 0 | 16.8 | 18.8823
| Sн. LV, МVА | 16+16 | 5120 | 1716 | 5.3999 | 3.05 |  | 2.3499 | 0 | 16.8 | 14.4501 |  |  |  | Sн. LV, МVА | 16+16 | 0.03 | 5.4299 | 3.05 | 0 | 2.3799 | 0 | 16.8 | 14.4201
45 | SS-110/6kv Donets | 40+40 | 26016 | 7584 | 27.0989 | 6.73 | 120 | 20.3689 | 0 | 42 | 21.6311 | 21.6311 |  | 45 | SS-110/6kv Donets | 40+40 | 2.605 | 29.7039 | 6.73 | 120 | 22.9739 | 0 | 42 | 19.0261 | #VALUE!
46 | SS-110/10kv Dubovoe | 40+40 | 23785 | 4642 | 24.2337 | 11.23 | 120 | 13.0037 | 0 | 42 | 28.9963 | 28.9963 |  | 46 | SS-110/10kv Dubovoe | 40+40 | 2.0873 | 26.321 | 11.23 | 120 | 15.091 | 0 | 42 | 26.909 | #VALUE!
47 | SS-110/35/6kv Zhuravliki | 40+25 | 23335 | 7691 | 24.5698 | 12.4 | 120 | 12.1698 | 0 | 42 | 29.8302 | 29.8302 |  | 47 | SS-110/35/6kv Zhuravliki | 40+25 | 0.415 | 24.9848 | 12.4 | 120 | 12.5848 | 0 | 42 | 29.4152 | #VALUE!
| Sн. MV, МVА | 40+25 | 16567 | 6202 | 17.6898 | 6.227 |  | 11.4628 | 0 | 42 | 30.5372 |  |  |  | Sн. MV, МVА | 40+25 | 0 | 17.6898 | 6.227 | 0 | 11.4628 | 0 | 42 | 30.5372
| Sн. LV, МVА | 40+25 | 6768 | 1489 | 6.9299 | 6.173 |  | 0.75686 | 0 | 42 | 41.2431 |  |  |  | Sн. LV, МVА | 40+25 | 0.415 | 7.3449 | 6.173 | 0 | 1.1719 | 0 | 42 | 40.8281
48 | SS-110/10kv Zapadnaya | 16+16 | 15459 | 3295 | 15.8063 | 1.249 | 80 | 14.5573 | 0 | 16.8 | 2.2427 | 2.2427 |  | 48 | SS-110/10kv Zapadnaya | 16+16 | 1.82 | 17.6263 | 1.249 | 80 | 16.3773 | 0 | 16.8 | 0.42274 | #VALUE!
49 | SS-110/35/10kv Ivnya | 10+10 | 5960 | 2270 | 6.3777 | 6.16 | 80 | 0.21766 | 0 | 10.5 | 10.2823 | 10.2823 |  | 49 | SS-110/35/10kv Ivnya | 10+10 | 0.085 | 6.4627 | 6.16 | 80 | 0.30266 | 0 | 10.5 | 10.1973 | 10.1973
| Sн. MV, МVА | 10+10 | 2266 | 1008 | 2.4801 | 2.375 |  | 0.10508 | 0 | 10.5 | 10.3949 |  |  |  | Sн. MV, МVА | 10+10 | 0 | 2.4801 | 2.375 | 0 | 0.10508 | 0 | 10.5 | 10.3949
| Sн. LV, МVА | 10+10 | 3694 | 1262 | 3.9036 | 3.785 |  | 0.11862 | 0 | 10.5 | 10.3814 |  |  |  | Sн. LV, МVА | 10+10 | 0.085 | 3.9886 | 3.785 | 0 | 0.20362 | 0 | 10.5 | 10.2964
50 | SS-110/35/10kv K.Gvardiya | 16+16 | 16357 | 6666 | 17.6632 | 7.7116 | 120 | 9.9516 | 0 | 16.8 | 6.8484 | 6.8484 |  | 50 | SS-110/35/10kv K.Gvardiya | 16+16 | 0.3655 | 18.0287 | 7.7116 | 120 | 10.3171 | 0 | 16.8 | 6.4829 | 6.4829
| Sн. MV, МVА | 16+16 | 8971 | 4110 | 9.8677 | 4.854 |  | 5.0137 | 0 | 16.8 | 11.7863 |  |  |  | Sн. MV, МVА | 16+16 | 0 | 9.8677 | 4.854 | 0 | 5.0137 | 0 | 16.8 | 11.7863
| Sн. LV, МVА | 16+16 | 7386 | 2556 | 7.8158 | 2.8576 |  | 4.9582 | 0 | 16.8 | 11.8418 |  |  |  | Sн. LV, МVА | 16+16 | 0.3655 | 8.1813 | 2.8576 | 0 | 5.3237 | 0 | 16.8 | 11.4763
51 | SS-110/10/6kv Kazatskie Bugry | 25+25 | 12571 | 3927 | 13.1701 | 9.65 | 80 | 3.5201 | 0 | 26.25 | 22.7299 | 18.8414 |  | 51 | SS-110/10/6kv Kazatskie Bugry | 25+25 | 0.015 | 13.1851 | 9.65 | 80 | 3.5351 | 0 | 26.25 | 22.7149 | 18.8264
| Sн. MV, МVА | 25+25 | 1720 | 404 | 1.7668 | 1.384 |  | 0.38281 | 0 | 26.25 | 25.8672 |  |  |  | Sн. MV, МVА | 25+25 | 0 | 1.7668 | 1.384 | 0 | 0.38281 | 0 | 26.25 | 25.8672
| Sн. LV, МVА | 25+25 | 10851 | 3523 | 11.4086 | 4 |  | 7.4086 | 0 | 26.25 | 18.8414 |  |  |  | Sн. LV, МVА | 25+25 | 0.015 | 11.4236 | 4 | 0 | 7.4236 | 0 | 26.25 | 18.8264
52 | SS-110/35/10kv Korocha | 16+16+16 | 20632 | 7838 | 22.0707 | 2.019 | 20 | 20.0517 | 0 | 21 | 0.94835 | 0.94835 |  | 52 | SS-110/35/10kv Korocha | 16+16+16 | 1.312 | 23.3827 | 2.019 | 20 | 21.3637 | 0 | 33.6 | 12.2363 | 12.2363
| Sн. MV, МVА | 16+16+16 | 8114 | 2802 | 8.5842 | 1.719 |  | 6.8652 | 0 | 21 | 14.1348 |  |  |  | Sн. MV, МVА | 16+16+16 | 0 | 8.5842 | 1.719 | 0 | 6.8652 | 0 | 33.6 | 26.7348
| Sн. LV, МVА | 16+16+16 | 12518 | 5036 | 13.493 | 0.3 |  | 13.193 | 0 | 21 | 7.807 |  |  |  | Sн. LV, МVА | 16+16+16 | 1.312 | 14.805 | 0.3 | 0 | 14.505 | 0 | 33.6 | 19.095
53 | SS-110/10kv Krapivenskaya | 16+16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.8 | 16.8 | 16.8 |  | 54 | SS-110/10kv Krapivenskaya | 16+16 | 0.65 | 0.65 | 0 | 0 | 0.65 | 0 | 16.8 | 16.15 | 16.15
54 | SS-110/35/10kv Krasnaya Yaruga | 10+10 | 9903 | 3556 | 10.5221 | 9.158 | 120 | 1.3641 | 0 | 10.5 | 9.1359 | 9.1359 |  | 54 | SS-110/35/10kv Krasnaya Yaruga | 10+10 | 0 | 10.5221 | 9.158 | 120 | 1.3641 | 0 | 10.5 | 9.1359 | 9.1359
| Sн. MV, МVА | 10+10 | 4393 | 1542 | 4.6558 | 3.52 |  | 1.1358 | 0 | 10.5 | 9.3642 |  |  |  | Sн. MV, МVА | 10+10 | 0 | 4.6558 | 3.52 | 0 | 1.1358 | 0 | 10.5 | 9.3642
| Sн. LV, МVА | 10+10 | 5510 | 2014 | 5.8665 | 5.638 |  | 0.22854 | 0 | 10.5 | 10.2715 |  |  |  | Sн. LV, МVА | 10+10 | 0 | 5.8665 | 5.638 | 0 | 0.22854 | 0 | 10.5 | 10.2715
55 | SS-110/10/10kv Mayskaya | 40+40 | 2581 | 670 | 2.6665 |  |  | 2.6665 | 0 | 42 | 39.3335 | 39.3335 |  | 55 | SS-110/10/10kv Mayskaya | 40+40 | 0.035 | 2.7015 | 0 | 0 | 2.7015 | 0 | 42 | 39.2985 | #VALUE!
56 | SS-110/35/10kv Maximovka | 16+16 | 7328 | 4264 | 8.4783 | 11.48 | 45 | -3.0017 | 0 | 16.8 | 19.8017 | 17.792 |  | 56 | SS-110/35/10kv Maximovka | 16+16 | 0 | 8.4783 | 11.48 | 45 | -3.0017 | 0 | 16.8 | 19.8017 | 17.792
| Sн. MV, МVА | 16+16 | 6384 | 3830 | 7.4448 | 9.449 |  | -2.0042 | 0 | 16.8 | 18.8042 |  |  |  | Sн. MV, МVА | 16+16 | 0 | 7.4448 | 9.449 | 0 | -2.0042 | 0 | 16.8 | 18.8042
| Sн. LV, МVА | 16+16 | 944 | 434 | 1.039 | 2.031 |  | -0.99201 | 0 | 16.8 | 17.792 |  |  |  | Sн. LV, МVА | 16+16 | 0 | 1.039 | 2.031 | 0 | -0.99201 | 0 | 16.8 | 17.792
57 | SS-110/35/10kv N.Oskol | 25+31,5 | 21159 | 8583 | 22.8336 | 9.119 | 80 | 13.7146 | 0 | 26.25 | 12.5354 | 12.5354 |  | 57 | SS-110/35/10kv N.Oskol | 25+31,5 | 0.305 | 23.1386 | 9.119 | 80 | 14.0196 | 0 | 26.25 | 12.2304 | 12.2304
| Sн. MV, МVА | 25+31,5 | 7395 | 3599 | 8.2243 | 7.83 |  | 0.39428 | 0 | 26.25 | 25.8557 |  |  |  | Sн. MV, МVА | 25+31,5 | 0 | 8.2243 | 7.83 | 0 | 0.39428 | 0 | 26.25 | 25.8557
| Sн. LV, МVА | 25+31,5 | 13764 | 4984 | 14.6386 | 1.289 |  | 13.3496 | 0 | 26.25 | 12.9004 |  |  |  | Sн. LV, МVА | 25+31,5 | 0.305 | 14.9436 | 1.289 | 0 | 13.6546 | 0 | 26.25 | 12.5954
58 | SS-110/10kv Obukhovskaya | 25+25 | 2272 | 372 | 2.3023 | 0 |  | 2.3023 | 0 | 26.25 | 23.9477 | 23.9477 |  | 58 | SS-110/10kv Obukhovskaya | 25+25 | 0 | 2.3023 | 0 | 0 | 2.3023 | 0 | 26.25 | 23.9477 | #VALUE!
59 | SS-110/6kv Ochistnye | 16+16 | 5231 | 2499 | 5.7973 | 0 |  | 5.7973 | 0 | 16.8 | 11.0027 | 11.0027 |  | 59 | SS-110/6kv Ochistnye | 16+16 | 0 | 5.7973 | 0 | 0 | 5.7973 | 0 | 16.8 | 11.0027 | #VALUE!
60 | SS-110/10kv Promyshlennaya | 25+25 | 15509 | 7413 | 17.1896 | 0 |  | 17.1896 | 0 | 26.25 | 9.0604 | 9.0604 |  | 60 | SS-110/10kv Promyshlennaya | 25+25 | 3.4417 | 20.6313 | 0 | 0 | 20.6313 | 0 | 26.25 | 5.6187 | #VALUE!
61 | SS-110/10kv Poultry plant | 16+16 | 9980 | 5649 | 11.4679 | 1.296 | 80 | 10.1719 | 0 | 16.8 | 6.6281 | 6.6281 |  | 61 | SS-110/10kv Poultry plant | 16+16 | 3.29 | 14.7579 | 1.296 | 80 | 13.4619 | 0 | 16.8 | 3.3381 | #VALUE!
62 | SS-110/10kv Pushkarnaya | 40+40 | 33540 | 9360 | 34.8216 | 0 | 60 | 34.8216 | 0 | 42 | 7.1784 | 7.1784 |  | 62 | SS-110/10kv Pushkarnaya | 40+40 | 0.088 | 34.9096 | 0 | 60 | 34.9096 | 0 | 42 | 7.0904 | #VALUE!
63 | SS-110/35/10kv Rakitnoe | 10+10 | 10160 | 3946 | 10.8994 | 8.98 | 120 | 1.9194 | 0 | 10.5 | 8.5806 | 7.7972 |  | 63 | SS-110/35/10kv Rakitnoe | 10+10 | 0.5586 | 11.458 | 8.98 | 120 | 2.478 | 0 | 10.5 | 8.022 | 7.2386
| Sн. MV, МVА | 10+10 | 4944 | 3154 | 5.8644 | 6.407 |  | -0.54263 | 0 | 10.5 | 11.0426 |  |  |  | Sн. MV, МVА | 10+10 | 0 | 5.8644 | 6.407 | 0 | -0.54263 | 0 | 10.5 | 11.0426
| Sн. LV, МVА | 10+10 | 5216 | 792 | 5.2758 | 2.573 |  | 2.7028 | 0 | 10.5 | 7.7972 |  |  |  | Sн. LV, МVА | 10+10 | 0.5586 | 5.8344 | 2.573 | 0 | 3.2614 | 0 | 10.5 | 7.2386
64 | SS-110/35/6kv Rudnik | 25+25 | 16284 | 8685 | 18.4553 | 10.46 | 45 | 7.9953 | 0 | 26.25 | 18.2547 | 18.2547 |  | 64 | SS-110/35/6kv Rudnik | 25+25 | 0.01 | 18.4653 | 10.46 | 45 | 8.0053 | 0 | 26.25 | 18.2447 | 18.2447
| Sн. MV, МVА | 25+25 | 10147 | 5511 | 11.547 | 10.46 |  | 1.087 | 0 | 26.25 | 25.163 |  |  |  | Sн. MV, МVА | 25+25 | 0 | 11.547 | 10.46 | 0 | 1.087 | 0 | 26.25 | 25.163
| Sн. LV, МVА | 25+25 | 6137 | 3174 | 6.9092 | 0 |  | 6.9092 | 0 | 26.25 | 19.3408 |  |  |  | Sн. LV, МVА | 25+25 | 0.01 | 6.9192 | 0 | 0 | 6.9192 | 0 | 26.25 | 19.3308
65 | SS-110/10kv Severnaya | 40+40 | 12059 | 3183 | 12.472 | 3.312 | 45 | 9.16 | 0 | 42 | 32.84 | 32.84 |  | 65 | SS-110/10kv Severnaya | 40+40 | 2.9216 | 15.3936 | 3.312 | 45 | 12.0816 | 0 | 42 | 29.9184 | #VALUE!
66 | SS-110/35/10kv Skorodnoe | 16+16 | 11370 | 3385 | 11.8632 | 10.36 | 120 | 1.5032 | 0 | 16.8 | 15.2968 | 15.2968 |  | 66 | SS-110/35/10kv Skorodnoe | 16+16 | 0.045 | 11.9082 | 10.36 | 120 | 1.5482 | 0 | 16.8 | 15.2518 | 15.2518
| Sн. MV, МVА | 16+16 | 7443 | 2214 | 7.7653 | 7.562 |  | 0.20331 | 0 | 16.8 | 16.5967 |  |  |  | Sн. MV, МVА | 16+16 | 0 | 7.7653 | 7.562 | 0 | 0.20331 | 0 | 16.8 | 16.5967
| Sн. LV, МVА | 16+16 | 3927 | 1171 | 4.0979 | 2.798 |  | 1.2999 | 0 | 16.8 | 15.5001 |  |  |  | Sн. LV, МVА | 16+16 | 0.045 | 4.1429 | 2.798 | 0 | 1.3449 | 0 | 16.8 | 15.4551
67 | SS-110/35/6kv St.Oskol - 1 | 20+25+25 | 27161 | 10201 | 29.0135 | 0 |  | 29.0135 | 0 | 47.25 | 18.2365 | 18.2365 |  | 67 | SS-110/35/6kv St.Oskol - 1 | 20+25+25 | 0.272 | 29.2855 | 0 | 0 | 29.2855 | 0 | 47.25 | 17.9645 | 17.9645
| Sн. MV, МVА | 20+25+25 | 5305 | 2289 | 5.7778 | 0 |  | 5.7778 | 0 | 47.25 | 41.4722 |  |  |  | Sн. MV, МVА | 20+25+25 | 0 | 5.7778 | 0 | 0 | 5.7778 | 0 | 47.25 | 41.4722
| Sн. LV, МVА | 20+25+25 | 21856 | 7912 | 23.244 | 0 |  | 23.244 | 0 | 47.25 | 24.006 |  |  |  | Sн. LV, МVА | 20+25+25 | 0.272 | 23.516 | 0 | 0 | 23.516 | 0 | 47.25 | 23.734
68 | SS-110/35/10kv Streletskaya | 16+16 | 6052 | 1769 | 6.3052 | 2.23 | 80 | 4.0752 | 0 | 16.8 | 12.7248 | 4.3575 |  | 68 | SS-110/35/10kv Streletskaya | 16+16 | 0.36285 | 6.6681 | 2.23 | 80 | 4.4381 | 0 | 16.8 | 12.3619 | 3.9946
| Sн. MV, МVА | 16+8 | 7 | 95 | 0.095258 | 0 |  | 0.095258 | 0 | 8.4 | 8.3047 |  |  |  | Sн. MV, МVА | 16+8 | 0 | 0.095258 | 0 | 0 | 0.095258 | 0 | 8.4 | 8.3047
| Sн. LV, МVА | 16+8 | 6045 | 1674 | 6.2725 | 2.23 |  | 4.0425 | 0 | 8.4 | 4.3575 |  |  |  | Sн. LV, МVА | 16+8 | 0.36285 | 6.6354 | 2.23 | 0 | 4.4054 | 0 | 8.4 | 3.9946
69 | SS-110/6kv Stroitel | 15+15 | 14665 | 5743 | 15.7494 | 0 |  | 15.7494 | 0 | 15.75 | 0.00057861 | 0.00057861 |  | 69 | SS-110/6kv Stroitel | 15+15 | 0.587 | 16.3364 | 0 | 0 | 16.3364 | 0 | 15.75 | -0.58642 | #VALUE!
70 | SS-110/35/10kv Tomarovka | 16+16 | 12522 | 4336 | 13.2515 | 3.46 | 45 | 9.7915 | 0 | 16.8 | 7.0085 | 7.0085 |  | 70 | SS-110/35/10kv Tomarovka | 16+16 | 0.09 | 13.3415 | 3.46 | 45 | 9.8815 | 0 | 16.8 | 6.9185 | #VALUE!
| Sн. MV, МVА | 16+16 | 4590 | 1614 | 4.8655 | 3.46 |  | 1.4055 | 0 | 16.8 | 15.3945 |  |  |  | Sн. MV, МVА | 16+16 | 0 | 4.8655 | 3.46 | 0 | 1.4055 | 0 | 16.8 | 15.3945
| Sн. LV, МVА | 16+16 | 7932 | 2722 | 8.3861 | 0 |  | 8.3861 | 0 | 16.8 | 8.4139 |  |  |  | Sн. LV, МVА | 16+16 | 0.09 | 8.4761 | 0 | 0 | 8.4761 | 0 | 16.8 | 8.3239
71 | SS-110/6kv Chemical plant | 32+32 | 8580 | 3308 | 9.1956 | 5.56 | 45 | 3.6356 | 0 | 33.6 | 29.9644 | 29.9644 |  | 71 | SS-110/6kv Chemical plant | 32+32 | 0.055 | 9.2506 | 5.56 | 45 | 3.6906 | 0 | 33.6 | 29.9094 | #VALUE!
72 | SS-110/10kv Tsentralnaya | 40+40 | 31170 | 5706 | 31.688 | 0 |  | 31.688 | 0 | 42 | 10.312 | 10.312 |  | 72 | SS-110/10kv Tsentralnaya | 40+40 | 0.826 | 32.514 | 0 | 0 | 32.514 | 0 | 42 | 9.486
73 | SS-110/35/10kv Cheremoshnoe | 25+25 | 23134 | 8712 | 24.7201 | 20.54 | 80 | 4.1801 | 0 | 26.25 | 22.0699 | 22.0699 |  | 73 | SS-110/35/10kv Cheremoshnoe | 25+25 | 0.014 | 24.7341 | 20.54 | 80 | 4.1941 | 0 | 26.25 | 22.0559 | 22.0559
| Sн. MV, МVА | 25+25 | 21521 | 7872 | 22.9155 | 19.676 |  | 3.2395 | 0 | 26.25 | 23.0105 |  |  |  | Sн. MV, МVА | 25+25 | 0 | 22.9155 | 19.676 | 0 | 3.2395 | 0 | 26.25 | 23.0105
| Sн. LV, МVА | 25+25 | 1613 | 840 | 1.8186 | 0 |  | 1.8186 | 0 | 26.25 | 24.4314 |  |  |  | Sн. LV, МVА | 25+25 | 0 | 1.8186 | 0 | 0 | 1.8186 | 0 | 26.25 | 24.4314
74 | SS-110/35/10kv Chernyanka | 16+16 | 16319 | 6059 | 17.4075 | 5.969 | 120 | 11.4385 | 0 | 16.8 | 5.3615 | 5.3615 |  | 74 | SS-110/35/10kv Chernyanka | 16+16 | 0.206 | 17.6135 | 5.969 | 120 | 11.6445 | 0 | 16.8 | 5.1555 | 5.1555
| Sн. MV, МVА | 16+16 | 7422 | 3146 | 8.0612 | 5.969 |  | 2.0922 | 0 | 16.8 | 14.7078 |  |  |  | Sн. MV, МVА | 16+16 | 0 | 8.0612 | 5.969 | 0 | 2.0922 | 0 | 16.8 | 14.7078
| Sн. LV, МVА | 16+16 | 8897 | 2913 | 9.3617 | 0 |  | 9.3617 | 0 | 16.8 | 7.4383 |  |  |  | Sн. LV, МVА | 16+16 | 0.206 | 9.5677 | 0 | 0 | 9.5677 | 0 | 16.8 | 7.2323
75 | SS-110/35/6kv Shebekino | 40+40 | 27508 | 12250 | 30.1123 | 16.65 | 120 | 13.4623 | 0 | 42 | 28.5377 | 28.5377 |  | 75 | SS-110/35/6kv Shebekino | 40+40 | 0.149 | 30.2613 | 16.65 | 120 | 13.6113 | 0 | 42 | 28.3887 | 28.3887
| Sн. MV, МVА | 40+40 | 15624 | 7736 | 17.4343 | 11.682 |  | 5.7523 | 0 | 42 | 36.2477 |  |  |  | Sн. MV, МVА | 40+40 | 0 | 17.4343 | 11.682 | 0 | 5.7523 | 0 | 42 | 36.2477
| Sн. LV, МVА | 40+40 | 11884 | 4514 | 12.7124 | 4.968 |  | 7.7444 | 0 | 42 | 34.2556 |  |  |  | Sн. LV, МVА | 40+40 | 0.149 | 12.8614 | 4.968 | 0 | 7.8934 | 0 | 42 | 34.1066
76 | SS-110/10kv Sheino | 3,2+10 | 2394 | 805 | 2.5257 | 0 |  | 2.5257 | 0 | 3.36 | 0.83428 | 0.83428 |  | 76 | SS-110/10kv Sheino | 3,2+10 | 0.038 | 2.5637 | 0 | 0 | 2.5637 | 0 | 3.36 | 0.79628 | #VALUE!
77 | SS-110/10/6kv Yuzhnaya | 40+40 | 44406 | 12168 | 46.0429 | 12.94 | 120 | 33.1029 | 0 | 42 | 8.8971 | 8.8971 |  | 77 | SS-110/10/6kv Yuzhnaya | 40+40 | 1.73 | 47.7729 | 12.94 | 120 | 34.8329 | 0 | 42 | 7.1671 | #VALUE!
| Sн. MV, МVА | 40+40 | 7092 | 1440 | 7.2367 | 3.42 |  | 3.8167 | 0 | 42 | 38.1833 |  |  |  | Sн. MV, МVА | 40+40 | 0 | 7.2367 | 3.42 | 0 | 3.8167 | 0 | 42 | 38.1833
| Sн. LV, МVА | 40+40 | 37314 | 10728 | 38.8256 | 9.52 |  | 29.3056 | 0 | 42 | 12.6944 |  |  |  | Sн. LV, МVА | 40+40 | 1.73 | 40.5556 | 9.52 | 0 | 31.0356 | 0 | 42 | 10.9644
78 | SS-35/10kv Aleynikovo | 2,5+2,5 | 776 | 312 | 0.83637 | 0.43267 | 120 | 0.40371 | 0 | 2.625 | 2.2213 | 2.2213 |  | 78 | SS-35/10kv Aleynikovo | 2,5+2,5 | 0.015 | 0.85137 | 0.43267 | 120 | 0.41871 | 0 | 2.625 | 2.2063 | #VALUE!
79 | SS-35/10kv Alexeevka (yak.) | 2,5+2,5 | 928 | 280 | 0.96932 | 0.46639 | 120 | 0.50293 | 0 | 2.625 | 2.1221 | 2.1221 |  | 79 | SS-35/10kv Alexeevka (yak.) | 2,5+2,5 | 0 | 0.96932 | 0.46639 | 120 | 0.50293 | 0 | 2.625 | 2.1221 | #VALUE!
80 | SS-35/10kv Alexeevka (kor.) | 4+4 | 872 | 312 | 0.92614 | 0 |  | 0.92614 | 0 | 4.2 | 3.2739 | 3.2739 |  | 80 | SS-35/10kv Alexeevka (kor.) | 4+4 | 0.06 | 0.98614 | 0 | 0 | 0.98614 | 0 | 4.2 | 3.2139 | #VALUE!
81 | SS-35/10kv Annovka | 2,5+2,5 | 1014 | 366 | 1.078 | 0.44652 | 80 | 0.63151 | 0 | 2.625 | 1.9935 | 1.9935 |  | 81 | SS-35/10kv Annovka | 2,5+2,5 | 0.015 | 1.093 | 0.44652 | 80 | 0.64651 | 0 | 2.625 | 1.9785 | #VALUE!
82 | SS-35/10kv Artelnoe | 6,3+6,3 | 3332 | 2520 | 4.1776 | 0.55 | 45 | 3.6276 | 0 | 6.615 | 2.9874 | 2.9874 |  | 82 | SS-35/10kv Artelnoe | 6,3+6,3 | 0.015 | 4.1926 | 0.55 | 45 | 3.6426 | 0 | 6.615 | 2.9724 | #VALUE!
83 | SS-35/10kv B.Dvory | 4+4 | 2632 | 912 | 2.7855 | 1.191 | 120 | 1.5945 | 0 | 4.2 | 2.6055 | 2.6055 |  | 83 | SS-35/10kv B.Dvory | 4+4 | 0.015 | 2.8005 | 1.191 | 120 | 1.6095 | 0 | 4.2 | 2.5905 | #VALUE!
84 | SS-35/10kv B.Ivanovka | 4+4 | 1136 | 448 | 1.2211 | 0.62488 | 80 | 0.59627 | 0 | 4.2 | 3.6037 | 3.6037 |  | 84 | SS-35/10kv B.Ivanovka | 4+4 | 0 | 1.2211 | 0.62488 | 80 | 0.59627 | 0 | 4.2 | 3.6037 | #VALUE!
85 | SS-35/10kv B.Kolodez | 2,5+2,5 | 1032 | 420 | 1.1142 | 0.44779 | 45 | 0.6664 | 0 | 2.625 | 1.9586 | 1.9586 |  | 85 | SS-35/10kv B.Kolodez | 2,5+2,5 | 0 | 1.1142 | 0.44779 | 45 | 0.6664 | 0 | 2.625 | 1.9586 | #VALUE!
86 | SS-35/10kv B.Ples | 2,5+2,5 | 808 | 408 | 0.90517 | 0.606 | 45 | 0.29917 | 0 | 2.625 | 2.3258 | 2.3258 |  | 86 | SS-35/10kv B.Ples | 2,5+2,5 | 0.015 | 0.92017 | 0.606 | 45 | 0.31417 | 0 | 2.625 | 2.3108 | #VALUE!
87 | SS-35/10kv B.Troitsa | 6,3+6,3 | 3564 | 1236 | 3.7722 | 2.83 | 45 | 0.94224 | 0 | 6.615 | 5.6728 | 5.6728 |  | 87 | SS-35/10kv B.Troitsa | 6,3+6,3 | 0.259 | 4.0312 | 2.83 | 45 | 1.2012 | 0 | 6.615 | 5.4138 | #VALUE!
88 | SS-35/10kv Belovskoe | 4+4 | 3592 | 1632 | 3.9454 | 1.21 | 80 | 2.7354 | 0 | 4.2 | 1.4646 | 1.4646 |  | 88 | SS-35/10kv Belovskoe | 4+4 | 0.105 | 4.0504 | 1.21 | 80 | 2.8404 | 0 | 4.2 | 1.3596 | #VALUE!
89 | SS-35/10kv Belyanka | 2,5+4 | 1936 | 800 | 2.0948 | 1.3214 | 45 | 0.77338 | 0 | 2.625 | 1.8516 | 1.8516 |  | 89 | SS-35/10kv Belyanka | 2,5+4 | 0.014 | 2.1088 | 1.3214 | 45 | 0.78738 | 0 | 2.625 | 1.8376 | #VALUE!
90 | SS-35/10kv Bessonovka | 6,3+6,3 | 6464 | 2896 | 7.0831 | 0.918 | 120 | 6.1651 | 0 | 6.615 | 0.44991 | 0.44991 |  | 90 | SS-35/10kv Bessonovka | 6,3+6,3 | 0.04 | 7.1231 | 0.918 | 120 | 6.2051 | 0 | 6.615 | 0.40991 | #VALUE!
91 | SS-35/10kv B.Lubyanki | 2,5+1,6 | 1208 | 368 | 1.2628 | 0.522 | 45 | 0.74081 | 0 | 1.68 | 0.93919 | 0.93919 |  | 91 | SS-35/10kv B.Lubyanki | 2,5+1,6 | 0.01 | 1.2728 | 0.522 | 45 | 0.75081 | 0 | 1.68 | 0.92919 | #VALUE!
92 | SS-35/10kv V.Mikhailovka | 4+4 | 2544 | 1200 | 2.8128 | 1.45 | 80 | 1.3628 | 0 | 4.2 | 2.8372 | 2.8372 |  | 92 | SS-35/10kv V.Mikhailovka | 4+4 | 0.04 | 2.8528 | 1.45 | 80 | 1.4028 | 0 | 4.2 | 2.7972 | #VALUE!
93 | SS-35/10kv Varvarovka | 2,5+2,5 | 1820 | 844 | 2.0062 | 1.0795 | 120 | 0.92663 | 0 | 2.625 | 1.6984 | 1.6984 |  | 93 | SS-35/10kv Varvarovka | 2,5+2,5 | 0.1219 | 2.1281 | 1.0795 | 120 | 1.0485 | 0 | 2.625 | 1.5765 | #VALUE!
94 | SS-35/10kv Vengerovka | 2,5+2,5 | 1056 | 324 | 1.1046 | 0.4 | 120 | 0.70459 | 0 | 2.625 | 1.9204 | 1.9204 |  | 94 | SS-35/10kv Vengerovka | 2,5+2,5 | 0.53 | 1.6346 | 0.4 | 120 | 1.2346 | 0 | 2.625 | 1.3904 | #VALUE!
95 | SS-35/10kv Verkhopenye | 2,5+4 | 1448 | 640 | 1.5831 | 1.0177 | 45 | 0.56548 | 0 | 2.625 | 2.0595 | 2.0595 |  | 95 | SS-35/10kv Verkhopenye | 2,5+4 | 0 | 1.5831 | 1.0177 | 45 | 0.56548 | 0 | 2.625 | 2.0595 | #VALUE!
96 | SS-35/10kv Viktoropol | 2,5+4 | 1328 | 456 | 1.4041 | 0.95536 | 120 | 0.44875 | 0 | 2.625 | 2.1762 | 2.1762 |  | 96 | SS-35/10kv Viktoropol | 2,5+4 | 0.01 | 1.4141 | 0.95536 | 120 | 0.45875 | 0 | 2.625 | 2.1662 | #VALUE!
97 | SS-35/10kv Vislaya Dubrava | 4+4 | 2616 | 756 | 2.723 | 0.616 | 80 | 2.107 | 0 | 4.2 | 2.093 | 2.093 |  | 97 | SS-35/10kv Vislaya Dubrava | 4+4 | 0 | 2.723 | 0.616 | 80 | 2.107 | 0 | 4.2 | 2.093 | #VALUE!
98 | SS-35/10kv Vladimirovka | 4+4 | 645 | 391 | 0.75426 | 0 |  | 0.75426 | 0 | 4.2 | 3.4457 | 3.4457 |  | 98 | SS-35/10kv Vladimirovka | 4+4 | 0 | 0.75426 | 0 | 0 | 0.75426 | 0 | 4.2 | 3.4457 | #VALUE!
99 | SS-35/10kv Water storage | 4+6,3 | 2136 | 420 | 2.1769 | 0.305 | 45 | 1.8719 | 0 | 4.2 | 2.3281 | 2.3281 |  | 99 | SS-35/10kv Water storage | 4+6,3 | 0 | 2.1769 | 0.305 | 45 | 1.8719 | 0 | 4.2 | 2.3281 | #VALUE!
100 | SS-35/6kv Vostochnaya | 6,3+6,3 | 4320 | 1469 | 4.5629 | 1.43 | 120 | 3.1329 | 0 | 6.615 | 3.4821 | 3.4821 |  | 100 | SS-35/6kv Vostochnaya | 6,3+6,3 | 0.027 | 4.5899 | 1.43 | 120 | 3.1599 | 0 | 6.615 | 3.4551 | #VALUE!
101 | SS-35/10kv Vsesvyatka | 2,5+2,5 | 1926 | 774 | 2.0757 | 0.99513 | 120 | 1.0806 | 0 | 2.625 | 1.5444 | 1.5444 |  | 101 | SS-35/10kv Vsesvyatka | 2,5+2,5 | 0.026 | 2.1017 | 0.99513 | 120 | 1.1066 | 0 | 2.625 | 1.5184 | #VALUE!
102 | SS-35/10kv Glinnoe | 6,3+6,3 | 2432 | 1600 | 2.9111 | 1.4036 | 80 | 1.5075 | 0 | 6.615 | 5.1075 | 5.1075 |  | 102 | SS-35/10kv Glinnoe | 6,3+6,3 | 0 | 2.9111 | 1.4036 | 80 | 1.5075 | 0 | 6.615 | 5.1075 | #VALUE!
103 | SS-35/10kv Golovchino | 2,5+2,5 | 2688 | 996 | 2.8666 | 0.617 | 45 | 2.2496 | 0 | 2.625 | 0.37541 | 0.37541 |  | 103 | SS-35/10kv Golovchino | 2,5+2,5 | 0.037 | 2.9036 | 0.617 | 45 | 2.2866 | 0 | 2.625 | 0.33841 | #VALUE!
104 | SS-35/10kv Gora-Podol | 2,5+4 | 1504 | 516 | 1.5901 | 0.9085 | 45 | 0.68155 | 0 | 2.625 | 1.9434 | 1.9434 |  | 104 | SS-35/10kv Gora-Podol | 2,5+4 | 0 | 1.5901 | 0.9085 | 45 | 0.68155 | 0 | 2.625 | 1.9434 | #VALUE!
105 | SS-35/10kv Gorodishche | 4+4 | 3232 | 1600 | 3.6064 | 0 |  | 3.6064 | 0 | 4.2 | 0.59364 | 0.59364 |  | 105 | SS-35/10kv Gorodishche | 4+4 | 0.025 | 3.6314 | 0 | 0 | 3.6314 | 0 | 4.2 | 0.56864 | #VALUE!
106 | SS-35/10kv Dmitrievka | 4+4 | 1200 | 528 | 1.311 | 0.78237 | 80 | 0.52865 | 0 | 4.2 | 3.6713 | 3.6713 |  | 106 | SS-35/10kv Dmitrievka | 4+4 | 0.4 | 1.711 | 0.78237 | 80 | 0.92865 | 0 | 4.2 | 3.2713 | #VALUE!
107 | SS-35/10kv Dorogoshch | 4+4 | 2600 | 936 | 2.7633 | 1.054 | 45 | 1.7093 | 0 | 4.2 | 2.4907 | 2.4907 |  | 107 | SS-35/10kv Dorogoshch | 4+4 | 0.084 | 2.8473 | 1.054 | 45 | 1.7933 | 0 | 4.2 | 2.4067 | #VALUE!
108 | SS-35/10kv Dragunka | 2,5+2,5 | 912 | 352 | 0.97757 | 0.62999 | 80 | 0.34758 | 0 | 2.625 | 2.2774 | 2.2774 |  | 108 | SS-35/10kv Dragunka | 2,5+2,5 | 0.01 | 0.98757 | 0.62999 | 80 | 0.35758 | 0 | 2.625 | 2.2674 | #VALUE!
109 | SS-35/10kv Zhuravlevka | 2,5+4 | 1216 | 336 | 1.2616 | 0.274 | 80 | 0.98757 | 0 | 2.625 | 1.6374 | 1.6374 |  | 109 | SS-35/10kv Zhuravlevka | 2,5+4 | 0.22 | 1.4816 | 0.274 | 80 | 1.2076 | 0 | 2.625 | 1.4174 | #VALUE!
110 | SS-35/6kv Zhuravliki | 10+10 | 7464 | 2112 | 7.7571 | 4.051 | 120 | 3.7061 | 0 | 10.5 | 6.7939 | 6.7939 |  | 110 | SS-35/6kv Zhuravliki | 10+10 | 0.3609 | 8.118 | 4.051 | 120 | 4.067 | 0 | 10.5 | 6.433 | #VALUE!
111 | SS-35/10kv Zavidovka | 2,5+2,5 | 606 | 282 | 0.6684 | 0.42 | 80 | 0.2484 | 0 | 2.625 | 2.3766 | 2.3766 |  | 111 | SS-35/10kv Zavidovka | 2,5+2,5 | 0.03 | 0.6984 | 0.42 | 80 | 0.2784 | 0 | 2.625 | 2.3466 | #VALUE!
112 | SS-35/6kv Zapadnaya | 10+10+10 | 6552 | 3360 | 7.3633 | 1.707 | 120 | 5.6563 | 0 | 21 | 15.3437 | 15.3437 |  | 112 | SS-35/6kv Zapadnaya | 10+10+10 | 0.06 | 7.4233 | 1.707 | 120 | 5.7163 | 0 | 21 | 15.2837 | #VALUE!
113 | SS-35/10kv Zozuli | 6,3+6,3 | 5744 | 3088 | 6.5214 | 3.88 | 80 | 2.6414 | 0 | 6.615 | 3.9736 | 3.9736 |  | 113 | SS-35/10kv Zozuli | 6,3+6,3 | 0.175 | 6.6964 | 3.88 | 80 | 2.8164 | 0 | 6.615 | 3.7986 | #VALUE!
114 | SS-35/10kv Ivitsa | 2,5+2,5 | 1192 | 392 | 1.2548 | 0.58603 | 80 | 0.66877 | 0 | 2.625 | 1.9562 | 1.9562 |  | 114 | SS-35/10kv Ivitsa | 2,5+2,5 | 1.444 | 2.6988 | 0.58603 | 80 | 2.1128 | 0 | 2.625 | 0.51223 | #VALUE!
115 | SS-35/10kv Ilovka | 4+4 | 2872 | 904 | 3.0109 | 2.056 | 45 | 0.95491 | 0 | 4.2 | 3.2451 | 3.2451 |  | 115 | SS-35/10kv Ilovka | 4+4 | 0.862 | 3.8729 | 2.056 | 45 | 1.8169 | 0 | 4.2 | 2.3831 | #VALUE!
116 | SS-35/10kv Istobnoe | 4+2,5 | 1224 | 632 | 1.3775 | 0.93935 | 120 | 0.43818 | 0 | 2.625 | 2.1868 | 2.1868 |  | 116 | SS-35/10kv Istobnoe | 4+2,5 | 0 | 1.3775 | 0.93935 | 120 | 0.43818 | 0 | 2.625 | 2.1868 | #VALUE!
117 | SS-35/10kv Kazatskaya | 2,5+4 | 1589 | 525 | 1.6735 | 0.87141 | 45 | 0.80207 | 0 | 2.625 | 1.8229 | 1.8229 |  | 117 | SS-35/10kv Kazatskaya | 2,5+4 | 0 | 1.6735 | 0.87141 | 45 | 0.80207 | 0 | 2.625 | 1.8229 | #VALUE!
118 | SS-35/10kv Kazinka | 4+4 | 2412 | 672 | 2.5039 | 0.736 | 120 | 1.7679 | 0 | 4.2 | 2.4321 | 2.4321 |  | 118 | SS-35/10kv Kazinka | 4+4 | 0.015 | 2.5189 | 0.736 | 120 | 1.7829 | 0 | 4.2 | 2.4171 | #VALUE!
119 | SS-35/10kv Kamyshevatoe | 2,5+2,5 | 1040 | 360 | 1.1005 | 0.712 | 120 | 0.38855 | 0 | 2.625 | 2.2365 | 2.2365 |  | 119 | SS-35/10kv Kamyshevatoe | 2,5+2,5 | 0.09 | 1.1905 | 0.712 | 120 | 0.47855 | 0 | 2.625 | 2.1465 | #VALUE!
120 | SS-35/10kv Kirovskaya | 6,3+6,3 | 3132 | 1536 | 3.4884 | 0.7035 | 120 | 2.7849 | 0 | 6.615 | 3.8301 | 3.8301 |  | 120 | SS-35/10kv Kirovskaya | 6,3+6,3 | 0.065 | 3.5534 | 0.7035 | 120 | 2.8499 | 0 | 6.615 | 3.7651 | #VALUE!
121 | SS-35/10kv Kotovo | 2,5+2,5 | 2672 | 768 | 2.7802 | 1.648 | 20 | 1.1322 | 0 | 2.625 | 1.4928 | 1.4928 |  | 121 | SS-35/10kv Kotovo | 2,5+2,5 | 0 | 2.7802 | 1.648 | 20 | 1.1322 | 0 | 2.625 | 1.4928 | #VALUE!
122 | SS-35/10kv Kochetovka | 2,5+4 | 858 | 294 | 0.90697 | 0.6286 | 45 | 0.27838 | 0 | 2.625 | 2.3466 | 2.3466 |  | 122 | SS-35/10kv Kochetovka | 2,5+4 | 0 | 0.90697 | 0.6286 | 45 | 0.27838 | 0 | 2.625 | 2.3466 | #VALUE!
123 | SS-35/10kv Krasnoe | 4+2,5 | 1128 | 424 | 1.2051 | 1.1395 | 80 | 0.065535 | 0 | 2.625 | 2.5595 | 2.5595 |  | 123 | SS-35/10kv Krasnoe | 4+2,5 | 0 | 1.2051 | 1.1395 | 80 | 0.065535 | 0 | 2.625 | 2.5595 | #VALUE!
124 | SS-35/10kv Kretovo | 4+2,5 | 1096 | 508 | 1.208 | 0.67818 | 120 | 0.52983 | 0 | 2.625 | 2.0952 | 2.0952 |  | 124 | SS-35/10kv Kretovo | 4+2,5 | 0.107 | 1.315 | 0.67818 | 120 | 0.63683 | 0 | 2.625 | 1.9882 | #VALUE!
125 | SS-35/10kv Kurasovka | 4+4 | 2800 | 1168 | 3.0338 | 1.797 | 80 | 1.2368 | 0 | 4.2 | 2.9632 | 2.9632 |  | 125 | SS-35/10kv Kurasovka | 4+4 | 0.03 | 3.0638 | 1.797 | 80 | 1.2668 | 0 | 4.2 | 2.9332 | #VALUE!
126 | SS-35/6kv Lebedi | 4+5,6 | 4392 | 1469 | 4.6312 | 0.581 | 120 | 4.0502 | 0 | 4.2 | 0.14984 | 0.14984 |  | 126 | SS-35/6kv Lebedi | 4+5,6 | 0.09 | 4.7212 | 0.581 | 120 | 4.1402 | 0 | 4.2 | 0.059842 | #VALUE!
127 | SS-35/6kv Ledovaya | 4+4 | 2578 | 1325 | 2.8986 | 1.321 | 80 | 1.5776 | 0 | 4.2 | 2.6224 | 2.6224 |  | 127 | SS-35/6kv Ledovaya | 4+4 | 0 | 2.8986 | 1.321 | 80 | 1.5776 | 0 | 4.2 | 2.6224 | #VALUE!
128 | SS-35/10kv Livenka | 4+4 | 3360 | 2364 | 4.1083 | 1.541 | 120 | 2.5673 | 0 | 4.2 | 1.6327 | 1.6327 |  | 128 | SS-35/10kv Livenka | 4+4 | 0.985 | 5.0933 | 1.541 | 120 | 3.5523 | 0 | 4.2 | 0.6477 | #VALUE!
129 | SS-35/10kv Lubyanoe | 2,5+2,5 | 828 | 336 | 0.89358 | 0.66672 | 80 | 0.22686 | 0 | 2.625 | 2.3981 | 2.3981 |  | 129 | SS-35/10kv Lubyanoe | 2,5+2,5 | 0 | 0.89358 | 0.66672 | 80 | 0.22686 | 0 | 2.625 | 2.3981 | #VALUE!
130 | SS-35/10kv M.Pristan | 6,3+6,3 | 6264 | 2844 | 6.8794 | 1.81 | 45 | 5.0694 | 0 | 6.615 | 1.5456 | 1.5456 |  | 130 | SS-35/10kv M.Pristan | 6,3+6,3 | 0.7663 | 7.6457 | 1.81 | 45 | 5.8357 | 0 | 6.615 | 0.77931 | #VALUE!
131 | SS-35/10kv М.Troitsa | 2,5+2,5 | 568 | 368 | 0.67679 | 0.60716 | 80 | 0.069632 | 0 | 2.625 | 2.5554 | 2.5554 |  | 131 | SS-35/10kv М.Troitsa | 2,5+2,5 | 0.02 | 0.69679 | 0.60716 | 80 | 0.089632 | 0 | 2.625 | 2.5354 | #VALUE!
132 | SS-35/10kv Malinovka | 10+10 | 5808 | 3776 | 6.9276 | 1.357 | 120 | 5.5706 | 0 | 10.5 | 4.9294 | 4.9294 |  | 132 | SS-35/10kv Malinovka | 10+10 | 0.04 | 6.9676 | 1.357 | 120 | 5.6106 | 0 | 10.5 | 4.8894 | #VALUE!
133 | SS-35/10kv Mandrovo | 2,5+2,5 | 1488 | 438 | 1.5511 | 0.65565 | 80 | 0.89548 | 0 | 2.625 | 1.7295 | 1.7295 |  | 133 | SS-35/10kv Mandrovo | 2,5+2,5 | 0.01 | 1.5611 | 0.65565 | 80 | 0.90548 | 0 | 2.625 | 1.7195 | #VALUE!
134 | SS-35/10kv Mukhouderovka | 2,5+2,5 | 1362 | 510 | 1.4544 | 0.643 | 80 | 0.81135 | 0 | 2.625 | 1.8136 | 1.8136 |  | 134 | SS-35/10kv Mukhouderovka | 2,5+2,5 | 0.031 | 1.4854 | 0.643 | 80 | 0.84235 | 0 | 2.625 | 1.7826 | #VALUE!
135 | SS-35/10kv N.Alexandrovka | 2,5+2,5 | 1110 | 522 | 1.2266 | 0.59315 | 120 | 0.63346 | 0 | 2.625 | 1.9915 | 1.9915 |  | 135 | SS-35/10kv N.Alexandrovka | 2,5+2,5 | 0 | 1.2266 | 0.59315 | 120 | 0.63346 | 0 | 2.625 | 1.9915 | #VALUE!
136 | SS-35/10kv N.Derevnya | 6,3+6,3 | 5888 | 1920 | 6.1931 | 2.78 | 120 | 3.4131 | 0 | 6.615 | 3.2019 | 3.2019 |  | 136 | SS-35/10kv N.Derevnya | 6,3+6,3 | 0.181 | 6.3741 | 2.78 | 120 | 3.5941 | 0 | 6.615 | 3.0209 | #VALUE!
137 | SS-35/10kv N.Tavolzhanka | 6,3+6,3 | 3360 | 912 | 3.4816 | 0.842 | 45 | 2.6396 | 0 | 6.615 | 3.9754 | 3.9754 |  | 137 | SS-35/10kv N.Tavolzhanka | 6,3+6,3 | 0.3192 | 3.8008 | 0.842 | 45 | 2.9588 | 0 | 6.615 | 3.6562 | #VALUE!
138 | SS-35/10kv N.Ukolovo | 4+2,5 | 1608 | 764 | 1.7803 | 0.57 | 80 | 1.2103 | 0 | 2.625 | 1.4147 | 1.4147 |  | 138 | SS-35/10kv N.Ukolovo | 4+2,5 | 1.245 | 3.0253 | 0.57 | 80 | 2.4553 | 0 | 2.625 | 0.16973 | #VALUE!
139 | SS-35/10kv N.Khutornoe | 2,5+4 | 294 | 142 | 0.3265 | 0.19 | 80 | 0.1365 | 0 | 2.625 | 2.4885 | 2.4885 |  | 139 | SS-35/10kv N.Khutornoe | 2,5+4 | 0.015 | 0.3415 | 0.19 | 80 | 0.1515 | 0 | 2.625 | 2.4735 | #VALUE!
140 | SS-35/10kv Neminushchee | 4+2,5 | 1474 | 706 | 1.6344 | 0.65147 | 80 | 0.98288 | 0 | 2.625 | 1.6421 | 1.6421 |  | 140 | SS-35/10kv Neminushchee | 4+2,5 | 0.08 | 1.7144 | 0.65147 | 80 | 1.0629 | 0 | 2.625 | 1.5621 | #VALUE!
141 | SS-35/10kv Nechaevka | 4+4 | 1328 | 392 | 1.3846 | 0.451 | 120 | 0.93365 | 0 | 4.2 | 3.2664 | 3.2664 |  | 141 | SS-35/10kv Nechaevka | 4+4 | 0.055 | 1.4396 | 0.451 | 120 | 0.98865 | 0 | 4.2 | 3.2114 | #VALUE!
142 | SS-35/10kv Nikitovka | 2,5+2,5 | 1888 | 744 | 2.0293 | 1.4354 | 80 | 0.59387 | 0 | 2.625 | 2.0311 | 2.0311 |  | 142 | SS-35/10kv Nikitovka | 2,5+2,5 | 0.168 | 2.1973 | 1.4354 | 80 | 0.76187 | 0 | 2.625 | 1.8631 | #VALUE!
143 | SS-35/10kv Novenkoe | 4+4 | 2216 | 964 | 2.4166 | 1.7332 | 80 | 0.68339 | 0 | 4.2 | 3.5166 | 3.5166 |  | 143 | SS-35/10kv Novenkoe | 4+4 | 0 | 2.4166 | 1.7332 | 80 | 0.68339 | 0 | 4.2 | 3.5166 | #VALUE!
144 | SS-35/10kv Oktyabrskaya | 6,3+6,3 | 7040 | 2384 | 7.4327 | 0.872 | 80 | 6.5607 | 0 | 6.615 | 0.054298 | 0.054298 |  | 144 | SS-35/10kv Oktyabrskaya | 6,3+6,3 | 0.494 | 7.9267 | 0.872 | 80 | 7.0547 | 0 | 6.615 | -0.4397 | #VALUE!
145 | SS-35/10kv Orlik | 4+4 | 2172 | 768 | 2.3038 | 0.553 | 80 | 1.7508 | 0 | 4.2 | 2.4492 | 2.4492 |  | 145 | SS-35/10kv Orlik | 4+4 | 0.012 | 2.3158 | 0.553 | 80 | 1.7628 | 0 | 4.2 | 2.4372 | #VALUE!
146 | SS-35/10kv Podolkhi | 2,5+2,5 | 1528 | 664 | 1.666 | 1.1225 | 45 | 0.54355 | 0 | 2.625 | 2.0815 | 2.0815 |  | 146 | SS-35/10kv Podolkhi | 2,5+2,5 | 0.42 | 2.086 | 1.1225 | 45 | 0.96355 | 0 | 2.625 | 1.6615 | #VALUE!
147 | SS-35/10kv Popovka | 6,3+4 | 1152 | 528 | 1.2672 | 0.64636 | 80 | 0.62088 | 0 | 4.2 | 3.5791 | 3.5791 |  | 147 | SS-35/10kv Popovka | 6,3+4 | 1.03 | 2.2972 | 0.64636 | 80 | 1.6509 | 0 | 4.2 | 2.5491 | #VALUE!
148 | SS-35/10kv Prelestnoe | 4+4 | 2268 | 780 | 2.3984 | 0 |  | 2.3984 | 0 | 4.2 | 1.8016 | 1.8016 |  | 148 | SS-35/10kv Prelestnoe | 4+4 | 0.085 | 2.4834 | 0 | 0 | 2.4834 | 0 | 4.2 | 1.7166 | #VALUE!
149 | SS-35/6kv Privokzalnaya | 6,3+6,3 | 5357 | 2160 | 5.7761 | 0 |  | 5.7761 | 0 | 6.615 | 0.83892 | 0.83892 |  | 149 | SS-35/6kv Privokzalnaya | 6,3+6,3 | 0.04 | 5.8161 | 0 | 0 | 5.8161 | 0 | 6.615 | 0.79892 | #VALUE!
150 | SS-35/10kv Prilepy | 2,5+2,5 | 544 | 360 | 0.65233 | 0.37638 | 80 | 0.27596 | 0 | 2.625 | 2.349 | 2.349 |  | 150 | SS-35/10kv Prilepy | 2,5+2,5 | 0 | 0.65233 | 0.37638 | 80 | 0.27596 | 0 | 2.625 | 2.349 | #VALUE!
151 | SS-35/10kv Printsevka | 2,5+2,5 | 1502 | 424 | 1.5607 | 0.352 | 120 | 1.2087 | 0 | 2.625 | 1.4163 | 1.4163 |  | 151 | SS-35/10kv Printsevka | 2,5+2,5 | 0.02 | 1.5807 | 0.352 | 120 | 1.2287 | 0 | 2.625 | 1.3963 | #VALUE!
152 | SS-35/10kv Radkovka | 6,3+6,3 | 2624 | 992 | 2.8053 | 0.164 | 45 | 2.6413 | 0 | 6.615 | 3.9737 | 3.9737 |  | 152 | SS-35/10kv Radkovka | 6,3+6,3 | 0.09 | 2.8953 | 0.164 | 45 | 2.7313 | 0 | 6.615 | 3.8837 | #VALUE!
153 | SS-35/10kv Razdornoe | 2,5+2,5 | 1314 | 576 | 1.4347 | 0.662 | 80 | 0.7727 | 0 | 2.625 | 1.8523 | 1.8523 |  | 153 | SS-35/10kv Razdornoe | 2,5+2,5 | 0 | 1.4347 | 0.662 | 80 | 0.7727 | 0 | 2.625 | 1.8523 | #VALUE!
154 | SS-35/10kv Repyakhovka | 2,5+2,5 | 1464 | 736 | 1.6386 | 0.88491 | 80 | 0.75368 | 0 | 2.625 | 1.8713 | 1.8713 |  | 154 | SS-35/10kv Repyakhovka | 2,5+2,5 | 0 | 1.6386 | 0.88491 | 80 | 0.75368 | 0 | 2.625 | 1.8713 | #VALUE!
155 | SS-35/10kv Rzhevka | 10+10 | 6576 | 3408 | 7.4066 | 2.53 | 45 | 4.8766 | 0 | 10.5 | 5.6234 | 5.6234 |  | 155 | SS-35/10kv Rzhevka | 10+10 | 0.135 | 7.5416 | 2.53 | 45 | 5.0116 | 0 | 10.5 | 5.4884 | #VALUE!
156 | SS-35/10kv Rovenki | 4+4 | 3240 | 1272 | 3.4807 | 1.7393 | 120 | 1.7414 | 0 | 4.2 | 2.4586 | 2.4586 |  | 156 | SS-35/10kv Rovenki | 4+4 | 0 | 3.4807 | 1.7393 | 120 | 1.7414 | 0 | 4.2 | 2.4586 | #VALUE!
157 | SS-35/10kv Rogovatoe | 2,5+2,5 | 1536 | 720 | 1.6964 | 0 |  | 1.6964 | 0 | 2.625 | 0.92862 | 0.92862 |  | 157 | SS-35/10kv Rogovatoe | 2,5+2,5 | 1.433 | 3.1294 | 0 | 0 | 3.1294 | 0 | 2.625 | -0.50438 | #VALUE!
158 | SS-35/10kv Saprykino | 2,5+2,5 | 384 | 192 | 0.42933 | 0.22751 | 120 | 0.20181 | 0 | 2.625 | 2.4232 | 2.4232 |  | 158 | SS-35/10kv Saprykino | 2,5+2,5 | 0.015 | 0.44433 | 0.22751 | 120 | 0.21681 | 0 | 2.625 | 2.4082 | #VALUE!
159 | SS-35/6kv Severnaya | 6,3+6,3 | 6264 | 1887 | 6.5421 | 4.8049 | 120 | 1.7371 | 0 | 6.615 | 4.8779 | 4.8779 |  | 159 | SS-35/6kv Severnaya | 6,3+6,3 | 0.0338 | 6.5759 | 4.8049 | 120 | 1.7709 | 0 | 6.615 | 4.8441 | #VALUE!
160 | SS-35/10kv Setishche | 2,5+2,5 | 1830 | 852 | 2.0186 | 1.0621 | 80 | 0.9565 | 0 | 2.625 | 1.6685 | 1.6685 |  | 160 | SS-35/10kv Setishche | 2,5+2,5 | 0.035 | 2.0536 | 1.0621 | 80 | 0.9915 | 0 | 2.625 | 1.6335 | #VALUE!
161 | SS-35/10kv Slonovka | 4+4 | 2224 | 1392 | 2.6237 | 1.1306 | 120 | 1.4931 | 0 | 4.2 | 2.7069 | 2.7069 |  | 161 | SS-35/10kv Slonovka | 4+4 | 0.85 | 3.4737 | 1.1306 | 120 | 2.3431 | 0 | 4.2 | 1.8569 | #VALUE!
162 | SS-35/6kv St.Oskol -2 | 16+16 | 11806 | 4574 | 12.6611 | 1.21 | 80 | 11.4511 | 0 | 16.8 | 5.3489 | 5.3489 |  | 162 | SS-35/6kv St.Oskol -2 | 16+16 | 0.209 | 12.8701 | 1.21 | 80 | 11.6601 | 0 | 16.8 | 5.1399 | #VALUE!
163 | SS-35/10kv Starikovo | 4+4 | 1464 | 660 | 1.6059 | 1.3453 | 45 | 0.26059 | 0 | 4.2 | 3.9394 | 3.9394 |  | 163 | SS-35/10kv Starikovo | 4+4 | 0 | 1.6059 | 1.3453 | 45 | 0.26059 | 0 | 4.2 | 3.9394 | #VALUE!
164 | SS-35/10kv Tavrovo | 10+10 | 8592 | 1296 | 8.6892 | 0.531 | 45 | 8.1582 | 0 | 10.5 | 2.3418 | 2.3418 |  | 164 | SS-35/10kv Tavrovo | 10+10 | 1.157 | 9.8462 | 0.531 | 45 | 9.3152 | 0 | 10.5 | 1.1848 | #VALUE!
165 | SS-35/10kv Terebrino | 2,5+2,5 | 1116 | 636 | 1.2845 | 0.44978 | 80 | 0.83472 | 0 | 2.625 | 1.7903 | 1.7903 |  | 165 | SS-35/10kv Terebrino | 2,5+2,5 | 0 | 1.2845 | 0.44978 | 80 | 0.83472 | 0 | 2.625 | 1.7903 | #VALUE!
166 | SS-35/10kv Urazovo | 6,3+6,3 | 4776 | 1524 | 5.0133 | 1.39 | 120 | 3.6233 | 0 | 6.615 | 2.9917 | 2.9917 |  | 166 | SS-35/10kv Urazovo | 6,3+6,3 | 0.13 | 5.1433 | 1.39 | 120 | 3.7533 | 0 | 6.615 | 2.8617 | #VALUE!
167 | SS-35/10kv Utochka | 1,6+2,5 | 682 | 272 | 0.73424 | 0.47242 | 80 | 0.26182 | 0 | 1.68 | 1.4182 | 1.4182 |  | 167 | SS-35/10kv Utochka | 1,6+2,5 | 0 | 0.73424 | 0.47242 | 80 | 0.26182 | 0 | 1.68 | 1.4182 | #VALUE!
168 | SS-35/6kv Fedoseevka | 4+4 | 2160 | 682 | 2.2651 | 0 |  | 2.2651 | 0 | 4.2 | 1.9349 | 1.9349 |  | 168 | SS-35/6kv Fedoseevka | 4+4 | 0.07 | 2.3351 | 0 | 0 | 2.3351 | 0 | 4.2 | 1.8649 | #VALUE!
169 | SS-35/10kv Foshchevatvo | 1,6+2,5 | 980 | 408 | 1.0615 | 0.78681 | 45 | 0.27473 | 0 | 1.68 | 1.4053 | 1.4053 |  | 169 | SS-35/10kv Foshchevatvo | 1,6+2,5 | 0.01 | 1.0715 | 0.78681 | 45 | 0.28473 | 0 | 1.68 | 1.3953 | #VALUE!
170 | SS-35/10kv Kholodnoe | 4+4 | 1708 | 516 | 1.7842 | 0 |  | 1.7842 | 0 | 4.2 | 2.4158 | 2.4158 |  | 170 | SS-35/10kv Kholodnoe | 4+4 | 0.025 | 1.8092 | 0 | 0 | 1.8092 | 0 | 4.2 | 2.3908 | #VALUE!
171 | SS-35/6kv Chernyansky sugar plant | 7,5+6,3 | 1608 | 1128 | 1.9642 | 1.3513 | 20 | 0.61293 | 0 | 6.615 | 6.0021 | 6.0021 |  | 171 | SS-35/6kv Chernyansky sugar plant | 7,5+6,3 | 0 | 1.9642 | 1.3513 | 20 | 0.61293 | 0 | 6.615 | 6.0021 | #VALUE!
172 | SS-35/10kv Shatalovka | 6,3+6,3 | 1928 | 736 | 2.0637 | 0 |  | 2.0637 | 0 | 6.615 | 4.5513 | 4.5513 |  | 172 | SS-35/10kv Shatalovka | 6,3+6,3 | 0.1 | 2.1637 | 0 | 0 | 2.1637 | 0 | 6.615 | 4.4513 | #VALUE!
173 | SS-35/10kv Shakhovka | 2,5+2,5 | 1596 | 588 | 1.7009 | 0.79066 | 80 | 0.91021 | 0 | 2.625 | 1.7148 | 1.7148 |  | 173 | SS-35/10kv Shakhovka | 2,5+2,5 | 0.052 | 1.7529 | 0.79066 | 80 | 0.96221 | 0 | 2.625 | 1.6628 | #VALUE!
174 | SS-35/10kv Shishino | 4+6,3 | 3456 | 904 | 3.5723 | 1.03 | 80 | 2.5423 | 0 | 4.2 | 1.6577 | 1.6577 |  | 174 | SS-35/10kv Shishino | 4+6,3 | 0.2 | 3.7723 | 1.03 | 80 | 2.7423 | 0 | 4.2 | 1.4577 | #VALUE!
175 | SS-35/10kv Yablonovo | 4+4 | 1664 | 688 | 1.8006 | 1.1284 | 80 | 0.6722 | 0 | 4.2 | 3.5278 | 3.5278 |  | 175 | SS-35/10kv Yablonovo | 4+4 | 0 | 1.8006 | 1.1284 | 80 | 0.6722 | 0 | 4.2 | 3.5278 | #VALUE!
176 | SS-35/10kv Yarskoe | 2,5+2,5 | 504 | 264 | 0.56896 | 0.14648 | 80 | 0.42248 | 0 | 2.625 | 2.2025 | 2.2025 |  | 176 | SS-35/10kv Yarskoe | 2,5+2,5 | 0 | 0.56896 | 0.14648 | 80 | 0.42248 | 0 | 2.625 | 2.2025 | #VALUE!
| TOTAL: | 3186.9 |  |  | 1131.8395 | #VALUE! |  | #VALUE! | [6 empty] | TOTAL: | 3186.9 | 64.7046 | #VALUE! | 453.9275 | 0 | #VALUE! | 0 | 0 | 0 | 0
| deficit | [10 empty] | -10.268 |  | 2: deficit; Min 12: #REF!
| proficit | [10 empty] | 897.8224 |  | 2: proficit; Min 12: 833.0636