## ЦП Текущий дефицит, табл.1
Форма расчёта пропускной способности Центров питания филиала ОАО "МРСК Центра" -"Курскэнерго"
по итогам зимнего замера максимума нагрузки 16.12.2009 г.
таблица 1
№п/п | Наименование объекта центра питания, класс напряжения | Текущий дефицит | [8 empty] | примечание
|  | Установленная мощность трансформаторов Sуст. с указанием их количества, шт/ МВА | Суммарная полная мощность ЦП по результатам замеров максимума нагрузки Sмах , МВА | Полная мощность, перераспределяемая в соответствии с ПТЭ, МВА за время |  | Полная мощность с учётом перераспределения, МВА | Ограничивающие факторы, МВА | Допустимая нагрузка расчётная в режиме n-1, МВА | Дефицит /профицит ЦП, МВА
|  |  |  | МВА | Мин.
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
Однотрансформаторные ПС
1 | ПС 110/35/10 Артюховка | 1*6,3 | 1.64 | 6.3 | 1 сутки | 6.3 | 0 | 6.3 | 4.66 | 1.2 | открыт
| Ном. Мощность СН, МВА | 6.3 | 1.1 | 2.3 | 1 сутки | 2.3 | 0 | 2.3 | 1.2
| Ном. Мощность НН, МВА | 6.3 | 0.54 | 4 | 1 сутки | 4 | 0 | 4 | 3.46
2 | ПС 110/10 Бекетово | 1*6,3 | 0.39 | 2.15 | 1 сутки | 2.15 | 0 | 2.15 | 1.76 | 1.76 | открыт
3 | ПС 110/35/10 Беседино | 1*6,3 | 2.84 | 6.7 | 1 сутки | 6.7 | 0 | 6.7 | 3.86 | 0.16 | открыт
| Ном. Мощность СН, МВА | 6.3 | 0.5 | 4.2 | 1 сутки | 4.2 | 0 | 4.2 | 3.7
| Ном. Мощность НН, МВА | 6.3 | 2.34 | 2.5 | 1 сутки | 2.5 | 0 | 2.5 | 0.16
4 | ПС 110/10 Восход | 1*10 | 0.8 | 2.5 | 1 сутки | 2.5 | 0 | 2.5 | 1.7 | 1.7 | открыт
5 | ПС 110/35/10 Журятино | 1*6,3 | 0.82 | 6 | 1 сутки | 6 | 0 | 6 | 5.18 | 1.48 | открыт
| Ном. Мощность СН, МВА | 6.3 | 0 | 3.7 | 1 сутки | 3.7 | 0 | 3.7 | 3.7
| Ном. Мощность НН, МВА | 6.3 | 0.82 | 2.3 | 1 сутки | 2.3 | 0 | 2.3 | 1.48
6 | ПС 110/35/10 Жуковка | 1*10 | 1.1 | 5.16 | 120 | 5.16 | 0 | 5.16 | 4.06 | 0.49 | открыт
| Ном. Мощность СН, МВА | 10 | 0.93 | 4.5 | 1 сутки | 4.5 | 0 | 4.5 | 3.57
| Ном. Мощность НН, МВА | 10 | 0.17 | 0.66 | 120 | 0.66 | 0 | 0.66 | 0.49
7 | ПС 110/10 Забелье | 1*2,5 | 0.31 | 2.15 | 1 сутки | 2.15 | 0 | 2.15 | 1.84 | 1.84 | открыт
8 | ПС 110/10 Ивница | 1*6,3 | 0.4 | 0.45 | 1 сутки | 0.45 | 0 | 0.45 | 0.05 | 0.05 | открыт
9 | ПС 110/35/10 Лачиново | 1*10 | 1.28 | 5.13 | 1 сутки | 5.13 | 0 | 5.13 | 3.85 | 1 | открыт
| Ном. Мощность СН, МВА | 10 | 0.75 | 3.6 | 1 сутки | 3.6 | 0 | 3.6 | 2.85
| Ном. Мощность НН, МВА | 10 | 0.53 | 1.53 | 1 сутки | 1.53 | 0 | 1.53 | 1
10 | ПС 110/10 Малая Локня | 1*10 | 1.2 | 1.21 | 1 сутки | 1.21 | 0 | 1.21 | 0.01 | 0.01 | открыт
11 | ПС 110/10 Марица | 1*2,5 | 0.99 | 1.92 | 1 сутки | 1.92 | 0 | 1.92 | 0.93 | 0.93 | открыт
12 | ПС 110/35/10 Расховец | 1*6,3 | 0.56 | 5.89 | 1 сутки | 5.89 | 0 | 5.89 | 5.33 | 1.97 | открыт
| Ном. Мощность СН, МВА | 6.3 | 0.38 | 3.74 | 1 сутки | 3.74 | 0 | 3.74 | 3.36
| Ном. Мощность НН, МВА | 6.3 | 0.18 | 2.15 | 1 сутки | 2.15 | 0 | 2.15 | 1.97
13 | ПС 110/10 Семеновская | 1*2,5 | 0.4 | 1.4 | 1 сутки | 1.4 | 0 | 1.4 | 1 | 1 | открыт
14 | ПС 110/6 Тепличная | 1*16 | 4.1 | 6.64 | 1 сутки | 6.64 | 0 | 6.64 | 2.54 | 2.54 | открыт
15 | ПС 110/35/10 Троицкая | 1*10 | 3.01 | 7.5 | 1 сутки | 7.5 | 0 | 7.5 | 4.49 | 0.79 | открыт
| Ном. Мощность СН, МВА | 10 | 2.7 | 6.4 | 1 сутки | 6.4 | 0 | 6.4 | 3.7
| Ном. Мощность НН, МВА | 10 | 0.31 | 1.1 | 1 сутки | 1.1 | 0 | 1.1 | 0.79
16 | ПС 35/10 Автодор | 1*2,5 | 0.46 | 0.8 | 1 сутки | 0.8 | 0 | 0.8 | 0.34 | 0.34 | открыт
17 | ПС 35/10 Агроном | 1*1,8 | 0.7 | 0.96 | 1 сутки | 0.96 | 0 | 0.96 | 0.26 | 0.26 | открыт
18 | ПС 35/10 Акимовка | 1*2,5 | 0.25 | 0.68 | 1 сутки | 0.68 | 0 | 0.68 | 0.43 | 0.43 | открыт
19 | ПС 35/10 Алексеевка | 1*2,5 | 0.28 | 1.43 | 1 сутки | 1.43 | 0 | 1.43 | 1.15 | 1.15 | открыт
20 | ПС 35/10 Афанасьевка (ЗЭС) | 1*4 | 0.55 | 1.34 | 1 сутки | 1.34 | 0 | 1.34 | 0.79 | 0.79 | открыт
21 | ПС 35/10 Б. Гнеушево | 1*2,5 | 0.77 | 0.96 | 1 сутки | 0.96 | 0 | 0.96 | 0.19 | 0.19 | открыт
22 | ПС 35/10 Б.Солдатское 1 | 1*3,2 | 0.78 | 2.83 | 1 сутки | 2.83 | 0 | 2.83 | 2.05 | 2.05 | открыт
23 | ПС 35/10 Банищи | 1*1,6 | 0.22 | 0.64 | 1 сутки | 0.64 | 0 | 0.64 | 0.42 | 0.42 | открыт
24 | ПС 35/10 Бараново | 1*4 | 0.46 | 1.43 | 1 сутки | 1.43 | 0 | 1.43 | 0.97 | 0.97 | открыт
25 | ПС 35/10 Белгородка | 1*2,5 | 0.27 | 2.15 | 1 сутки | 2.15 | 0 | 2.15 | 1.88 | 1.88 | открыт
26 | ПС 35/10 Белица | 1*4 | 0.6 | 1.76 | 1 сутки | 1.76 | 0 | 1.76 | 1.16 | 1.16 | открыт
27 | ПС 35/10 Бирюковка | 1*1,6 | 0.6 | 0.67 | 1 сутки | 0.67 | 0 | 0.67 | 0.07 | 0.07 | открыт
28 | ПС 35/10 Бобровка | 1*1,6 | 0.24 | 0.67 | 1 сутки | 0.67 | 0 | 0.67 | 0.43 | 0.43 | открыт
29 | ПС 35/10 Боброво | 1*2,5 | 0.42 | 0.76 | 1 сутки | 0.76 | 0 | 0.76 | 0.34 | 0.34 | открыт
30 | ПС 35/10 Будки | 1*1 | 0.09 | 0.64 | 1 сутки | 0.64 | 0 | 0.64 | 0.55 | 0.55 | открыт
31 | ПС 35/10 Букреевка (ЦЭС) | 1*1,8 | 0.59 | 1.6 | 50 | 1.6 | 0 | 1.6 | 1.01 | 1.01 | открыт
32 | ПС 35/10 Букреевка (ЗЭС) | 1*1,6 | 0.21 | 0.64 | 1 сутки | 0.64 | 0 | 0.64 | 0.43 | 0.43 | открыт
33 | ПС 35/10 Бурцевка | 1*1,6 | 0.18 | 1.43 | 1 сутки | 1.43 | 0 | 1.43 | 1.25 | 1.25 | открыт
34 | ПС 35/10 Быково | 1*4 | 0.89 | 1.43 | 1 сутки | 1.43 | 0 | 1.43 | 0.54 | 0.54 | открыт
35 | ПС 35/10 В. Щигор | 1*2,5 | 0.12 | 2.15 | 1 сутки | 2.15 | 0 | 2.15 | 2.03 | 2.03 | открыт
36 | ПС 35/10 Ванино | 1*2,5 | 0.36 | 0.8 | 1 сутки | 0.8 | 0 | 0.8 | 0.44 | 0.44 | открыт
37 | ПС 35/10 Васильевка | 1*2,5 | 0.64 | 1.05 | 1 сутки | 1.05 | 0 | 1.05 | 0.41 | 0.41 | открыт
38 | ПС 35/10 Водохранилище | 1*4 | 1.58 | 2.72 | 1 сутки | 2.72 | 0 | 2.72 | 1.14 | 1.14 | открыт
39 | ПС 35/10 Волоконск | 1*2,5 | 0.3 | 1.1 | 1 сутки | 1.1 | 0 | 1.1 | 0.8 | 0.8 | открыт
40 | ПС 35/10 Воробьевка | 1*2,5 | 0.65 | 0.9 | 1 сутки | 0.9 | 0 | 0.9 | 0.25 | 0.25 | открыт
41 | ПС 35/10 Воронок | 1*4 | 0.86 | 2.1 | 1 сутки | 2.1 | 0 | 2.1 | 1.24 | 1.24 | открыт
42 | ПС 35/10 Вязовое | 1*2,5 | 0.66 | 2.15 | 1 сутки | 2.15 | 0 | 2.15 | 1.49 | 1.49 | открыт
43 | ПС 35/10 Гахово | 1*2,5 | 0.21 | 1.8 | 1 сутки | 1.8 | 0 | 1.8 | 1.59 | 1.59 | открыт
44 | ПС 35/10 Генеральшино | 1*2,5 | 0.25 | 1.5 | 1 сутки | 1.5 | 0 | 1.5 | 1.25 | 1.25 | открыт
45 | ПС 35/10 Глазово | 1*2,5 | 0.94 | 1.4 | 1 сутки | 1.4 | 0 | 1.4 | 0.46 | 0.46 | открыт
46 | ПС 35/10 Глебово | 1*2,5 | 0.49 | 1.4 | 1 сутки | 1.4 | 0 | 1.4 | 0.91 | 0.91 | открыт
47 | ПС 35/10 Гордеевка | 1*1,6 | 0.12 | 0.7 | 1 сутки | 0.7 | 0 | 0.7 | 0.58 | 0.58 | открыт
48 | ПС 35/10 Городенск | 1*1,6 | 0.59 | 0.76 | 1 сутки | 0.76 | 0 | 0.76 | 0.17 | 0.17 | открыт
49 | ПС 35/10 Горяйново | 1*2,5 | 0.5 | 1.1 | 1 сутки | 1.1 | 0 | 1.1 | 0.6 | 0.6 | открыт
50 | ПС 35/10 12-й Госконезавод | 1*2,5 | 0.53 | 1.43 | 1 сутки | 1.43 | 0 | 1.43 | 0.9 | 0.9 | открыт
51 | ПС 35/10 Грайворонка | 1*2,5 | 0.5 | 1.43 | 1 сутки | 1.43 | 0 | 1.43 | 0.93 | 0.93 | открыт
52 | ПС 35/10 Гриневка | 1*2,5 | 0.28 | 2.85 | 1 сутки | 2.85 | 0 | 2.85 | 2.57 | 2.57 | открыт
53 | ПС 35/10 Густомой | 1*1,6 | 0.21 | 0.94 | 1 сутки | 0.94 | 0 | 0.94 | 0.73 | 0.73 | открыт
54 | ПС 35/10 Дарьино | 1*2,5 | 0.4 | 1.8 | 1 сутки | 1.8 | 0 | 1.8 | 1.4 | 1.4 | открыт
55 | ПС 35/10 Демякино | 1*2,5 | 0.43 | 0.8 | 1 сутки | 0.8 | 0 | 0.8 | 0.37 | 0.37 | открыт
56 | ПС 35/10 Ефросимовка | 1*1,8 | 0.38 | 1.07 | 1 сутки | 1.07 | 0 | 1.07 | 0.69 | 0.69 | открыт
57 | ПС 35/10 Жданово | 1*2,5 | 0.38 | 0.85 | 1 сутки | 0.85 | 0 | 0.85 | 0.47 | 0.47 | открыт
58 | ПС 35/10 Защитное | 1*1,6 | 0.32 | 2.15 | 1 сутки | 2.15 | 0 | 2.15 | 1.83 | 1.83 | открыт
59 | ПС 35/10 Званное | 1*2,5 | 0.6 | 0.84 | 1 сутки | 0.84 | 0 | 0.84 | 0.24 | 0.24 | открыт
60 | ПС 35/10 Знаменка | 1*1,8 | 1.01 | 2.15 | 1 сутки | 2.15 | 0 | 2.15 | 1.14 | 1.14 | открыт
61 | ПС 35/10 Искра | 1*2,5 | 0.16 | 0.58 | 1 сутки | 0.58 | 0 | 0.58 | 0.42 | 0.42 | открыт
62 | ПС 35/10 Казанка | 1*4 | 0.33 | 0.8 | 1 сутки | 0.8 | 0 | 0.8 | 0.47 | 0.47 | открыт
63 | ПС 35/10 Калиновка (новая) | 1*2,5 | 0.17 | 1.8 | 1 сутки | 1.8 | 0 | 1.8 | 1.63 | 1.63 | открыт
64 | ПС 35/10 Карыж | 1*1,6 | 0.18 | 0.64 | 1 сутки | 0.64 | 0 | 0.64 | 0.46 | 0.46 | открыт
65 | ПС 35/10 Китаевка | 1*1,6 | 0.26 | 0.74 | 1 сутки | 0.74 | 0 | 0.74 | 0.48 | 0.48 | открыт
66 | ПС 35/10 Кобылки | 1*2,5 | 0.68 | 1.53 | 1 сутки | 1.53 | 0 | 1.53 | 0.85 | 0.85 | открыт
67 | ПС 35/10 Колонтаевка | 1*2,5 | 0.26 | 0.84 | 1 сутки | 0.84 | 0 | 0.84 | 0.58 | 0.58 | открыт
68 | ПС 35/10 Кондратовка | 1*1,8 | 0.55 | 1.42 | 1 сутки | 1.42 | 0 | 1.42 | 0.87 | 0.87 | открыт
69 | ПС 35/10 Коровяковка | 1*1,6 | 0.21 | 0.76 | 1 сутки | 0.76 | 0 | 0.76 | 0.55 | 0.55 | открыт
70 | ПС 35/10 Леженьки | 1*2,5 | 0.09 | 1.43 | 1 сутки | 1.43 | 0 | 1.43 | 1.34 | 1.34 | открыт
71 | ПС 35/10 Ленинская | 1*1,8 | 0.67 | 0.73 | 1 сутки | 0.73 | 0 | 0.73 | 0.06 | 0.06 | открыт
72 | ПС 35/10 Лобазовка | 1*2,5 | 0.86 | 1.09 | 1 сутки | 1.09 | 0 | 1.09 | 0.23 | 0.23 | открыт
73 | ПС 35/10 Луговка | 1*1,6 | 0.54 | 1.29 | 1 сутки | 1.29 | 0 | 1.29 | 0.75 | 0.75 | открыт
74 | ПС 35/10 Любава | 1*6,3 | 0.31 | 1.15 | 1 сутки | 1.15 | 0 | 1.15 | 0.84 | 0.84 | открыт
75 | ПС 35/10 Любимовка-1 | 1*3,2 | 0 | 0.96 | 1 сутки | 0.96 | 0 | 0.96 | 0.96 | 0.96 | открыт
76 | ПС 35/10 М. Каменец | 1*1,6 | 0.6 | 1.1 | 1 сутки | 1.1 | 0 | 1.1 | 0.5 | 0.5 | открыт
77 | ПС 35/10 М. Гнеушево | 1*4 | 0.7 | 1.28 | 1 сутки | 1.28 | 0 | 1.28 | 0.58 | 0.58 | открыт
78 | ПС 35/10 М. Крюки | 1*2,5 | 0.4 | 1.19 | 1 сутки | 1.19 | 0 | 1.19 | 0.79 | 0.79 | открыт
79 | ПС 35/10 Марково | 1*2,5 | 0.65 | 0.8 | 1 сутки | 0.8 | 0 | 0.8 | 0.15 | 0.15 | открыт
80 | ПС 35/10 Мармыжи | 1*2,5 | 0.21 | 1.33 | 1 сутки | 1.33 | 0 | 1.33 | 1.12 | 1.12 | открыт
81 | ПС 35/10 Меловое | 1*4 | 0.99 | 2.15 | 1 сутки | 2.15 | 0 | 2.15 | 1.16 | 1.16 | открыт
82 | ПС 35/10 Моква | 1*4 | 0.5 | 2.15 | 1 сутки | 2.15 | 0 | 2.15 | 1.65 | 1.65 | открыт
83 | ПС 35/10 Мокрушино | 1*1,6 | 0.6 | 1.1 | 1 сутки | 1.1 | 0 | 1.1 | 0.5 | 0.5 | открыт
84 | ПС 35/10 Молотычи | 1*2,5 | 0.4 | 0.9 | 1 сутки | 0.9 | 0 | 0.9 | 0.5 | 0.5 | открыт
85 | ПС 35/10 Мочаки | 1*2,5 | 0.03 | 1.07 | 1 сутки | 1.07 | 0 | 1.07 | 1.04 | 1.04 | открыт
86 | ПС 35/10 Н. Владимировка | 1*2,5 | 0.08 | 4.3 | 1 сутки | 4.3 | 0 | 4.3 | 4.22 | 4.22 | открыт
87 | ПС 35/10 Н. Гурово | 1*4,0 | 0.73 | 2.15 | 1 сутки | 2.15 | 0 | 2.15 | 1.42 | 1.42 | открыт
88 | ПС 35/10 Надейка | 1*2,5 | 0.16 | 1.4 | 1 сутки | 1.4 | 0 | 1.4 | 1.24 | 1.24 | открыт
89 | ПС 35/10 Нива | 1*2,5 | 0.4 | 1.56 | 1 сутки | 1.56 | 0 | 1.56 | 1.16 | 1.16 | открыт
90 | ПС 35/10 Ольговка | 1*2,5 | 0.41 | 0.97 | 1 сутки | 0.97 | 0 | 0.97 | 0.56 | 0.56 | открыт
91 | ПС 35/10 Ольховатка | 1*4 | 0.38 | 0.64 | 1 сутки | 0.64 | 0 | 0.64 | 0.26 | 0.26 | открыт
92 | ПС 35/10 Оросительная | 1*4 | 0.93 | 2.97 | 1 сутки | 2.97 | 0 | 2.97 | 2.04 | 2.04 | открыт
93 | ПС 35/10 Пены-2 | 1*2,5 | 0.6 | 2.32 | 1 сутки | 2.32 | 0 | 2.32 | 1.72 | 1.72 | открыт
94 | ПС 35/10 Переступлино (стар) | 1*2,5 | 0.16 | 1.4 | 1 сутки | 1.4 | 0 | 1.4 | 1.24 | 1.24 | открыт
95 | ПС 35/10 Переступлино (нов) | 1*2,5 | 0.36 | 1.4 | 1 сутки | 1.4 | 0 | 1.4 | 1.04 | 1.04 | открыт
96 | ПС 35/10 Петрово | 1*6,3 | 1 | 2.15 | 1 сутки | 2.15 | 0 | 2.15 | 1.15 | 1.15 | открыт
97 | ПС 35/10 Петровская | 1*2,5 | 0.03 | 0.74 | 1 сутки | 0.74 | 0 | 0.74 | 0.71 | 0.71 | открыт
98 | ПС 35/10 Покровское | 1*2,5 | 0.27 | 2.15 | 1 сутки | 2.15 | 0 | 2.15 | 1.88 | 1.88 | открыт
99 | ПС 35/10 Прилепы | 1*1,6 | 0.53 | 2.15 | 1 сутки | 2.15 | 0 | 2.15 | 1.62 | 1.62 | открыт
100 | ПС 35/10 Пристень | 1*4 | 2.3 | 3.3 | 1 сутки | 3.3 | 0 | 3.3 | 1 | 1 | открыт
101 | ПС 35/10 Р. Буды 35/10 | 1*4 | 0 | 0.74 | 1 сутки | 0.74 | 0 | 0.74 | 0.74 | 0.74 | открыт
102 | ПС 35/10 Реут | 1*2,5 | 0.16 | 0.86 | 0 | 0.86 | 0 | 0.86 | 0.7 | 0.7 | открыт
103 | ПС 35/10 Ровенка | 1*1,6 | 0.16 | 1.43 | 1 сутки | 1.43 | 0 | 1.43 | 1.27 | 1.27 | открыт
104 | ПС 35/10 Родина (СЭС) | 1*2,5 | 0.17 | 0.7 | 1 сутки | 0.7 | 0 | 0.7 | 0.53 | 0.53 | открыт
105 | ПС 35/10 Родина (ВЭС) | 1*4 | 0.5 | 2.3 | 1 сутки | 2.3 | 0 | 2.3 | 1.8 | 1.8 | открыт
106 | ПС 35/10 Рубанщина | 1*2,5 | 0.4 | 1.31 | 1 сутки | 1.31 | 0 | 1.31 | 0.91 | 0.91 | открыт
107 | ПС 35/10 Русаново | 1*1,8 | 0.39 | 1.43 | 1 сутки | 1.43 | 0 | 1.43 | 1.04 | 1.04 | открыт
108 | ПС 35/10 Рышково | 1*2,5 | 0.56 | 0.94 | 1 сутки | 0.94 | 0 | 0.94 | 0.38 | 0.38 | открыт
109 | ПС 35/10 Рязаново | 1*1,6 | 0.58 | 1.15 | 1 сутки | 1.15 | 0 | 1.15 | 0.57 | 0.57 | открыт
110 | ПС 35/10 Сазановка | 1*2,5 | 0.3 | 1.25 | 1 сутки | 1.25 | 0 | 1.25 | 0.95 | 0.95 | открыт
111 | ПС 35/10 Сергиевка | 1*2,5 | 0.4 | 2.7 | 1 сутки | 2.7 | 0 | 2.7 | 2.3 | 2.3 | открыт
112 | ПС 35/10 Соколье | 1*2,5 | 0.3 | 1.43 | 1 сутки | 1.43 | 0 | 1.43 | 1.13 | 1.13 | открыт
113 | ПС 35/10 Солнцево | 1*2,5 | 0.9 | 1.76 | 1 сутки | 1.76 | 0 | 1.76 | 0.86 | 0.86 | открыт
114 | ПС 35/10 Спасское | 1*1,6 | 0.22 | 1.1 | 1 сутки | 1.1 | 0 | 1.1 | 0.88 | 0.88 | открыт
115 | ПС 35/10 Ср. Ольшанка | 1*2,5 | 0.3 | 1.4 | 1 сутки | 1.4 | 0 | 1.4 | 1.1 | 1.1 | открыт
116 | ПС 35/10 Стрелецкая | 1*2,5 | 0.35 | 1.3 | 1 сутки | 1.3 | 0 | 1.3 | 0.95 | 0.95 | открыт
117 | ПС 35/10 Субботино | 1*2,5 | 0.6 | 1.34 | 1 сутки | 1.34 | 0 | 1.34 | 0.74 | 0.74 | открыт
118 | ПС 35/10 Сухая | 1*1,6 | 0.44 | 0.71 | 1 сутки | 0.71 | 0 | 0.71 | 0.27 | 0.27 | открыт
119 | ПС 35/10 Тельмана | 1*2,5 | 0.3 | 1.15 | 1 сутки | 1.15 | 0 | 1.15 | 0.85 | 0.85 | открыт
120 | ПС 35/10 Теребуж | 1*2,5 | 0.46 | 1.43 | 1 сутки | 1.43 | 0 | 1.43 | 0.97 | 0.97 | открыт
121 | ПС 35/10 Фатеевка | 1*2,5 | 0.08 | 0.7 | 1 сутки | 0.7 | 0 | 0.7 | 0.62 | 0.62 | открыт
122 | ПС 35/10 Фентисово | 1*1,6 | 0.17 | 1.72 | 1 сутки | 1.72 | 0 | 1.72 | 1.55 | 1.55 | открыт
123 | ПС 35/10 Чапаевская | 1*2,5 | 0.2 | 1.1 | 1 сутки | 1.1 | 0 | 1.1 | 0.9 | 0.9 | открыт
124 | ПС 35/10 Чемерки | 1*1,6 | 0.06 | 0.85 | 1 сутки | 0.85 | 0 | 0.85 | 0.79 | 0.79 | открыт
125 | ПС 35/10 Чижовка | 1*1,6 | 0.35 | 1.43 | 1 сутки | 1.43 | 0 | 1.43 | 1.08 | 1.08 | открыт
126 | ПС 35/10 Шатиловка | 1*2,5 | 0.16 | 1.43 | 1 сутки | 1.43 | 0 | 1.43 | 1.27 | 1.27 | открыт
127 | ПС 35/10 Шептуховка | 1*2,5 | 0.75 | 1.47 | 1 сутки | 1.47 | 0 | 1.47 | 0.72 | 0.72 | открыт
128 | ПС 35/10 Шуклино | 1*2,5 | 0.25 | 0.85 | 1 сутки | 0.85 | 0 | 0.85 | 0.6 | 0.6 | открыт
129 | ПС 35/10 Элеватор | 1*6,3 | 0.31 | 0.6 | 1 сутки | 0.6 | 0 | 0.6 | 0.29 | 0.29 | открыт
130 | ПС 35/10 Яньково | 1*1,6 | 0.25 | 0.64 | 1 сутки | 0.64 | 0 | 0.64 | 0.39 | 0.39 | открыт
131 | ПС 35/10 Ясенки | 1*2,5 | 0.48 | 2.15 | 1 сутки | 2.15 | 0 | 2.15 | 1.67 | 1.67 | открыт
Двух- и более трансформаторные ПС
1 | ПС 110/6 Аккумуляторная | 2*25 | 10.47 | 0 | 0 | 10.47 | 0 | 26.25 | 15.78 | 15.78 | открыт
2 | ПС 110/10 АРЗ | 6,3+10 | 2.62 | 0.9 | 45 | 1.72 | 0 | 6.62 | 4.9 | 4.9 | открыт
3 | ПС 110/35/10 Атомград | 2*25 | 13.07 | 20.2 | 120 | -7.13 | 0 | 26.25 | 33.38 | 26.02 | открыт
| Ном. Мощность СН, МВА | 25 | 3.24 | 10.6 | 120 | -7.36 | 0 | 26.25 | 33.61
| Ном. Мощность НН, МВА | 25 | 9.83 | 9.6 | 120 | 0.23 | 0 | 26.25 | 26.02
4 | ПС 110/10 Б. Жирово | 2*6,3 | 0.36 | 0.6 | 120 | -0.24 | 0 | 6.62 | 6.86 | 6.86 | открыт
5 | ПС 110/35/10 Басово | 5,6+10 | 1.19 | 6.19 | 15 | -5 | 0 | 5.88 | 10.88 | 5.38 | открыт
| Ном. Мощность СН, МВА | 5,6+10 | 0.5 | 6 |  | -5.5 | 0 | 5.88 | 11.38
| Ном. Мощность НН, МВА | 5,6+10 | 0.69 | 0.19 | 120 | 0.5 | 0 | 5.88 | 5.38
6 | ПС 110/35/10 Белая | 2*16 | 8.4 | 12 | 120 | -3.6 | 0 | 16.8 | 20.4 | 13.4 | открыт
| Ном. Мощность СН, МВА | 16 | 3.4 | 0 |  | 3.4 | 0 | 16.8 | 13.4
| Ном. Мощность НН, МВА | 16 | 5 | 12 | 120 | -7 | 0 | 16.8 | 23.8
7 | ПС 110/35/10 Бобрышово | 2*6,3 | 1.2 | 1.3 | 120 | -0.1 | 0 | 6.62 | 6.72 | 6.02 | открыт
| Ном. Мощность СН, МВА | 6.3 | 0.6 |  |  | 0.6 | 0 | 6.62 | 6.02
| Ном. Мощность НН, МВА | 6.3 | 0.6 | 1.3 | 120 | -0.7 | 0 | 6.62 | 7.32
8 | ПС 110/10 Винниково | 2,5+6,3 | 2.31 | 1.17 | 45 | 1.14 | 0 | 2.63 | 1.49 | 1.49 | открыт
9 | ПС 110/35/6 Волокно | 40+2*40,5 | 37.58 | 16.8 | 0 | 20.78 | 0 | 84.53 | 63.75 | 61.28 | открыт
| Ном. Мощность СН, МВА | 40+2*40,5 | 14.33 | 16.8 | 0 | -2.47 | 0 | 84.53 | 87
| Ном. Мощность НН, МВА | 40+2*40,5 | 23.25 | 0 | 0 | 23.25 | 0 | 84.53 | 61.28
10 | ПС 110/10 Высокая* | 2*16 | 28.27 | 3.2 | 15 | 25.07 | 0 | 16.8 | -8.27 | -8.27 | закрыт*
11 | ПС 110/35/10 Глушково | 2*10 | 8.7 | 8.04 | 120 | 0.66 | 0 | 10.5 | 9.84 | 8.44 | открыт
| Ном. Мощность СН, МВА | 10 | 5.2 | 6.6 | 120 | -1.4 | 0 | 10.5 | 11.9
| Ном. Мощность НН, МВА | 10 | 3.5 | 1.44 | 80 | 2.06 | 0 | 10.5 | 8.44
12 | ПС 110/10 Городская | 2*25 | 10.4 | 0 | 0 | 10.4 | 0 | 26.25 | 15.85 | 15.85 | открыт
13 | ПС 110/35/10 Горшечное | 10+16 | 9.41 | 6.52 | 120 | 2.89 | 0 | 10.5 | 7.61 | 7.61 | открыт
| Ном. Мощность СН, МВА | 10+16 | 6.13 | 6.06 |  | 0.07 | 0 | 10.5 | 10.43
| Ном. Мощность НН, МВА | 10+16 | 3.28 | 0.46 | 120 | 2.82 | 0 | 10.5 | 7.68
14 | ПС 110/35/10 Дмитриев | 2*10 | 7.09 | 10.4 | 120 | -3.31 | 0 | 10.5 | 13.81 | 8.43 | открыт
| Ном. Мощность СН, МВА | 10 | 2.02 | 7.4 |  | -5.38 | 0 | 10.5 | 15.88
| Ном. Мощность НН, МВА | 10 | 5.07 | 3 | 80 | 2.07 | 0 | 10.5 | 8.43
15 | ПС 110/6 Долгие Буды | 2*10 | 0.8 | 0.5 | 120 | 0.3 | 0 | 10.5 | 10.2 | 10.2 | открыт
16 | ПС 110/35/10 Золотухино | 2*25 | 6.76 | 23.57 | 80 | -16.81 | 0 | 26.25 | 43.06 | 25.59 | открыт
| Ном. Мощность СН, МВА | 25 | 2.8 | 18.8 |  | -16 | 0 | 26.25 | 42.25
| Ном. Мощность НН, МВА | 25 | 3.96 | 3.3 | 120 | 0.66 | 0 | 26.25 | 25.59
17 | ПС 110/35/10 Камыши | 2*6,3 | 8.59 | 5.45 | 20 | 3.14 | 0 | 6.62 | 3.48 | 3.07 | открыт
| Ном. Мощность СН, МВА | 6.3 | 7 | 3.45 |  | 3.55 | 0 | 6.62 | 3.07
| Ном. Мощность НН, МВА | 6.3 | 1.59 | 2 | 20 | -0.41 | 0 | 6.62 | 7.03
18 | ПС 110/35/10 Касторное | 15+16 | 14.13 | 6.97 | 120 | 7.16 | 0 | 15.75 | 8.59 | 8.59 | открыт
| Ном. Мощность СН, МВА | 15+16 | 10.63 | 6.6 |  | 4.03 | 0 | 15.75 | 11.72
| Ном. Мощность НН, МВА | 15+16 | 3.5 | 0.37 | 120 | 3.13 | 0 | 15.75 | 12.62
19 | ПС 110/35/10 Киликино | 2*16 | 2.53 | 6.9 | 120 | -4.37 | 0 | 16.8 | 21.17 | 18.51 | открыт
| Ном. Мощность СН, МВА | 16 | 2.34 | 5 |  | -2.66 | 0 | 16.8 | 19.46
| Ном. Мощность НН, МВА | 16 | 0.19 | 1.9 | 120 | -1.71 | 0 | 16.8 | 18.51
20 | ПС 110/35/6 Кировская | 2*40 | 53.66 | 16.36 | 120 | 37.3 | 0 | 42 | 4.7 | 4.7 | открыт
| Ном. Мощность СН, МВА | 40 | 26.67 | 13.06 | 120 | 13.61 | 0 | 42 | 28.39
| Ном. Мощность НН, МВА | 40 | 26.99 | 3.3 | 120 | 23.69 | 0 | 42 | 18.31
21 | ПС 110/35/10 Клюква | 2*16 | 3.28 | 1.2 | 120 | 2.08 | 0 | 16.8 | 14.72 | 14.72 | открыт
| Ном. Мощность СН, МВА | 16 | 0 |  |  | 0 | 0 | 16.8 | 16.8
| Ном. Мощность НН, МВА | 16 | 3.28 | 1.2 | 120 | 2.08 | 0 | 16.8 | 14.72
22 | ПС 110/10 Компрессорная | 2*40 | 1.11 | 0 | 0 | 1.11 | 0 | 42 | 40.89 | 40.89 | открыт
23 | ПС 110/35/10 Конышевка | 10+16 | 9.06 | 8 | 120 | 1.06 | 0 | 10.5 | 9.44 | 9.44 | открыт
| Ном. Мощность СН, МВА | 10+16 | 6.94 | 5.9 |  | 1.04 | 0 | 10.5 | 9.46
| Ном. Мощность НН, МВА | 10+16 | 2.12 | 2.1 |  | 0.02 | 0 | 10.5 | 10.48
24 | ПС 110/10 Котельная | 10+25 | 7.8 | 2.1 | 0 | 5.7 | 0 | 10.5 | 4.8 | 4.8 | открыт
25 | ПС 110/35/10 Кшень | 2*10 | 8.73 | 6.63 | 10 | 2.1 | 0 | 10.5 | 8.4 | 6.59 | открыт
| Ном. Мощность СН, МВА | 10 | 4.25 | 6.06 |  | -1.81 | 0 | 10.5 | 12.31
| Ном. Мощность НН, МВА | 10 | 4.48 | 0.57 | 120 | 3.91 | 0 | 10.5 | 6.59
26 | ПС 110/6 Лесная | 2*40 | 2.37 | 0 | 0 | 2.37 | 0 | 42 | 39.63 | 39.63 | открыт
27 | ПС 110/35/10 Льгов | 2*25 | 13.14 | 4 | 120 | 9.14 | 0 | 26.25 | 17.11 | 3.02 | открыт
| Ном. Мощность СН, МВА | 25 | 1.66 |  |  | 1.66 | 0 | 10.5 | 8.84
| Ном. Мощность НН, МВА | 25 | 11.48 | 4 | 120 | 7.48 | 0 | 10.5 | 3.02
28 | ПС 110/35/10 Лукашевка | 2*16 | 8.27 | 10.6 | 120 | -2.33 | 0 | 16.8 | 19.13 | 17.03 | открыт
| Ном. Мощность СН, МВА | 16 | 5.07 | 5.3 |  | -0.23 | 0 | 16.8 | 17.03
| Ном. Мощность НН, МВА | 16 | 3.2 | 5.3 | 120 | -2.1 | 0 | 16.8 | 18.9
29 | ПС 110/35/10 Любостань | 6,3+10 | 5.6 | 13.1 | 120 | -7.5 | 0 | 6.62 | 14.12 | 7.32 | открыт
| Ном. Мощность СН, МВА | 6,3+10 | 5 | 11.8 |  | -6.8 | 0 | 6.62 | 13.42
| Ном. Мощность НН, МВА | 6,3+10 | 0.6 | 1.3 |  | -0.7 | 0 | 6.62 | 7.32
30 | ПС 110/35/6 Мантурово | 2*16 | 6.58 | 9.35 | 10 | -2.77 | 0 | 16.8 | 19.57 | 16.86 | открыт
| Ном. Мощность СН, МВА | 16 | 6.38 | 9.09 |  | -2.71 | 0 | 16.8 | 19.51
| Ном. Мощность НН, МВА | 16 | 0.2 | 0.26 | 120 | -0.06 | 0 | 16.8 | 16.86
31 | ПС 110/35/10 8-е Марта | 6,3+10 | 7.07 | 9.6 | 120 | -2.53 | 0 | 6.62 | 9.15 | 7.41 | открыт
| Ном. Мощность СН, МВА | 6,3+10 | 5.81 | 6.6 | 120 | -0.79 | 0 | 6.62 | 7.41
| Ном. Мощность НН, МВА | 6,3+10 | 1.26 | 3 | 45 | -1.74 | 0 | 6.62 | 8.36
32 | ПС 110/10 Мартовская | 2*6,3 | 0.74 | 0.55 | 120 | 0.19 | 0 | 6.62 | 6.43 | 6.43 | открыт
33 | ПС 110/35/10 Марьино | 10+25 | 6.15 | 8.11 | 120 | -1.96 | 0 | 10.5 | 12.46 | 11.27 | открыт
| Ном. Мощность СН, МВА | 10+25 | 3.71 | 4.9 |  | -1.19 | 0 | 10.5 | 11.69
| Ном. Мощность НН, МВА | 10+25 | 2.44 | 3.21 |  | -0.77 | 0 | 10.5 | 11.27
34 | ПС 110/35/10 Медвенка | 2*10 | 5.95 | 19.22 | 120 | -13.27 | 0 | 10.5 | 23.77 | 8.74 | открыт
| Ном. Мощность СН, МВА | 10 | 2.07 | 17.1 |  | -15.03 | 0 | 10.5 | 25.53
| Ном. Мощность НН, МВА | 10 | 3.88 | 2.12 | 120 | 1.76 | 0 | 10.5 | 8.74
35 | ПС 110/6 Нефтяная | 2*10 | 0.28 |  |  | 0.28 | 0 | 10.5 | 10.22 | 10.22 | открыт
36 | ПС 110/35/10 Обоянь | 16 + 25 | 16.1 | 26.86 | 120 | -10.76 | 0 | 16.8 | 27.56 | 12.16 | открыт
| Ном. Мощность СН, МВА | 16 + 25 | 2 | 17.4 | 0 | -15.4 | 0 | 16.8 | 32.2
| Ном. Мощность НН, МВА | 16 + 25 | 14.1 | 9.46 |  | 4.64 | 0 | 16.8 | 12.16
37 | ПС 110/35/10 Октябрьская | 2*16 | 8.62 | 15.5 | 120 | -6.88 | 0 | 16.8 | 23.68 | 14.72 | открыт
| Ном. Мощность СН, МВА | 16 | 5.54 | 14.5 |  | -8.96 | 0 | 16.8 | 25.76
| Ном. Мощность НН, МВА | 16 | 3.08 | 1 | 120 | 2.08 | 0 | 16.8 | 14.72
38 | ПС 110/35/10 Ольховка | 2*6,3 | 1.92 | 6.31 | 120 | -4.39 | 0 | 6.62 | 11.01 | 7.71 | открыт
| Ном. Мощность СН, МВА | 6.3 | 1.7 | 5 | 120 | -3.3 | 0 | 6.62 | 9.92
| Ном. Мощность НН, МВА | 6.3 | 0.22 | 1.31 | 120 | -1.09 | 0 | 6.62 | 7.71
39 | ПС 110/10 Паники | 2*2,5 | 0.79 | 0.1 | 120 | 0.69 | 0 | 2.63 | 1.94 | 1.94 | открыт
40 | ПС 110/35/10 Пены | 2*16,0 | 9.63 | 6.9 | 120 | 2.73 | 0 | 16.8 | 14.07 | 14.07 | открыт
| Ном. Мощность СН, МВА | 16 | 4.37 | 3.5 |  | 0.87 | 0 | 16.8 | 15.93
| Ном. Мощность НН, МВА | 16 | 5.26 | 3.4 | 120 | 1.86 | 0 | 16.8 | 14.94
41 | ПС 110/35/10 Прибор | 2*25 | 32.12 | 6.5 | 0 | 25.62 | 0 | 26.25 | 0.63 | 0.63 | открыт
| Ном. Мощность СН, МВА | 25 | 0 |  |  | 0 | 0 | 26.25 | 26.25
| Ном. Мощность НН, МВА | 25 | 32.12 | 6.5 | 0 | 25.62 | 0 | 26.25 | 0.63
42 | ПС 110/10 Прогресс | 2*63 | 23.2 | 0 | 0 | 23.2 | 0 | 66.2 | 43 | 43 | открыт
43 | ПС 110/10 ПТФ | 6,3+10 | 5.92 | 0 | 0 | 5.92 | 0 | 6.62 | 0.7 | 0.7 | открыт
44 | ПС 110/35/10 Р. Буды | 2*10,0 | 3.4 | 15.7 | 120 | -12.3 | 0 | 10.5 | 22.8 | 15.5 | открыт
| Ном. Мощность СН, МВА | 10 | 2 | 9.3 |  | -7.3 | 0 | 10.5 | 17.8
| Ном. Мощность НН, МВА | 10 | 1.4 | 6.4 |  | -5 | 0 | 10.5 | 15.5
45 | ПС 110/35/10 Разиньково | 6,3+10 | 2.9 | 21.4 | 45 | -18.5 | 0 | 6.62 | 25.12 | 9.27 | открыт
| Ном. Мощность СН, МВА | 6,3+10 | 1.95 | 17.8 |  | -15.85 | 0 | 6.62 | 22.47
| Ном. Мощность НН, МВА | 6,3+10 | 0.95 | 3.6 | 45 | -2.65 | 0 | 6.62 | 9.27
46 | ПС 110/35/10 Рудная | 2*31,5 | 20.09 | 3.25 | 10 | 16.84 | 0 | 33.1 | 16.26 | 16.26 | открыт
| Ном. Мощность СН, МВА | 31.5 | 14.23 | 1.7 |  | 12.53 | 0 | 33.1 | 20.57
| Ном. Мощность НН, МВА | 31.5 | 5.86 | 1.55 | 120 | 4.31 | 0 | 33.1 | 28.79
47 | ПС 110/35/10 Рыльск | 16+25 | 18.95 | 11 | 120 | 7.95 | 0 | 16.8 | 8.85 | 8.85 | открыт
| Ном. Мощность СН, МВА | 16+25 | 12.9 | 7 |  | 5.9 | 0 | 16.8 | 10.9
| Ном. Мощность НН, МВА | 16+25 | 6.05 | 4 | 120 | 2.05 | 0 | 16.8 | 14.75
48 | ПС 110/10 Соловьиная | 2*25 | 6.91 | 0 | 0 | 6.91 | 0 | 26.25 | 19.34 | 19.34 | открыт
49 | ПС 110/10 СТК | 2*10 | 1.91 | 0 | 0 | 1.91 | 0 | 10.5 | 8.59 | 8.59 | открыт
50 | ПС 110/10 Студенок | 2*6,3 | 3.62 | 0.7 | 120 | 2.92 | 0 | 6.62 | 3.7 | 3.7 | открыт
51 | ПС 110/35/10 Суджа | 2*25 | 16.5 | 29 | 120 | -12.5 | 0 | 26.25 | 38.75 | 28.05 | открыт
| Ном. Мощность СН, МВА | 25 | 6.4 | 17.1 |  | -10.7 | 0 | 26.25 | 36.95
| Ном. Мощность НН, МВА | 25 | 10.1 | 11.9 |  | -1.8 | 0 | 26.25 | 28.05
52 | ПС 110/35/10 Счетмаш | 2*25 | 13.6 | 0 | 0 | 13.6 | 0 | 26.25 | 12.65 | 12.65 | открыт
| Ном. Мощность СН, МВА | 25 | 3.9 |  |  | 3.9 | 0 | 26.25 | 22.35
| Ном. Мощность НН, МВА | 25 | 9.7 | 0 | 0 | 9.7 | 0 | 26.25 | 16.55
53 | ПС 110/35/10 Теткино | 2*10 | 5.51 | 3.44 | 120 | 2.07 | 0 | 10.5 | 8.43 | 7.63 | открыт
| Ном. Мощность СН, МВА | 10 | 1.2 | 2 |  | -0.8 | 0 | 10.5 | 11.3
| Ном. Мощность НН, МВА | 10 | 4.31 | 1.44 |  | 2.87 | 0 | 10.5 | 7.63
54 | ПС 110/35/10 Тим | 6,3+16 | 5.7 | 9.59 | 120 | -3.89 | 0 | 6.62 | 10.51 | 5.02 | открыт
| Ном. Мощность СН, МВА | 6,3+16 | 3.6 | 9.09 |  | -5.49 | 0 | 6.62 | 12.11
| Ном. Мощность НН, МВА | 6,3+16 | 2.1 | 0.5 | 120 | 1.6 | 0 | 6.62 | 5.02
55 | ПС 110/35/10 Уютное | 10+16 | 1.01 | 0.5 | 120 | 0.51 | 0 | 10.5 | 9.99 | 9.83 | открыт
| Ном. Мощность СН, МВА | 10+16 | 0.67 |  |  | 0.67 | 0 | 10.5 | 9.83
| Ном. Мощность НН, МВА | 10+16 | 0.34 | 0.5 | 120 | -0.16 | 0 | 10.5 | 10.66
56 | ПС 110/35/10 Фатеж | 2*16 | 6.32 | 17.4 | 120 | -11.08 | 0 | 16.8 | 27.88 | 17.08 | открыт
| Ном. Мощность СН, МВА | 16 | 2 | 12.8 |  | -10.8 | 0 | 16.8 | 27.6
| Ном. Мощность НН, МВА | 16 | 4.32 | 4.6 | 120 | -0.28 | 0 | 16.8 | 17.08
57 | ПС 110/35/10 Фосфоритная | 2*25 | 5.44 | 12.34 | 120 | -6.9 | 0 | 26.25 | 33.15 | 24.41 | открыт
| Ном. Мощность СН, МВА | 25 | 3.38 | 12.12 |  | -8.74 | 0 | 26.25 | 34.99
| Ном. Мощность НН, МВА | 25 | 2.06 | 0.22 | 10 | 1.84 | 0 | 26.25 | 24.41
58 | ПС 110/35/10 Хомутовка | 7,5+10 | 5.69 | 6.3 | 80 | -0.61 | 0 | 7.88 | 8.49 | 5.32 | открыт
| Ном. Мощность СН, МВА | 7,5+10 | 0.73 | 3.9 |  | -3.17 | 0 | 7.88 | 11.05
| Ном. Мощность НН, МВА | 7,5+10 | 4.96 | 2.4 | 80 | 2.56 | 0 | 7.88 | 5.32
59 | ПС 110/35/10 Черемисиново | 2*16 | 6.15 | 9.38 | 10 | -3.23 | 0 | 16.8 | 20.03 | 15.06 | открыт
| Ном. Мощность СН, МВА | 16 | 4.12 | 9.09 |  | -4.97 | 0 | 16.8 | 21.77
| Ном. Мощность НН, МВА | 16 | 2.03 | 0.29 | 120 | 1.74 | 0 | 16.8 | 15.06
60 | ПС 110/35/10 Черемошки | 2*6,3 | 3.34 | 8.25 | 120 | -4.91 | 0 | 6.62 | 11.53 | 7.09 | открыт
| Ном. Мощность СН, МВА | 6.3 | 2.56 | 7 |  | -4.44 | 0 | 6.62 | 11.06
| Ном. Мощность НН, МВА | 6.3 | 0.78 | 1.25 | 129 | -0.47 | 0 | 6.62 | 7.09
61 | ПС 110/35/10 Шумаково | 2*10 | 4.4 | 13.73 | 120 | -9.33 | 0 | 10.5 | 19.83 | 12.03 | открыт
| Ном. Мощность СН, МВА | 10 | 3.4 | 11.2 |  | -7.8 | 0 | 10.5 | 18.3
| Ном. Мощность НН, МВА | 10 | 1 | 2.53 | 120 | -1.53 | 0 | 10.5 | 12.03
62 | ПС 110/35/10 Щигры | 2*25 | 11.28 | 12.9 | 120 | -1.62 | 0 | 26.5 | 28.12 | 21.55 | открыт
| Ном. Мощность СН, МВА | 25 | 5.55 | 12.12 |  | -6.57 | 0 | 26.5 | 33.07
| Ном. Мощность НН, МВА | 25 | 5.73 | 0.78 | 120 | 4.95 | 0 | 26.5 | 21.55
63 | ПС 110/35/10 Ястребовка | 7,5+10 | 2.56 | 6.31 | 10 | -3.75 | 0 | 7.88 | 11.63 | 6.95 | открыт
| Ном. Мощность СН, МВА | 7,5+10 | 1.38 | 6.06 |  | -4.68 | 0 | 7.88 | 12.56
| Ном. Мощность НН, МВА | 7,5+10 | 1.18 | 0.25 | 10 | 0.93 | 0 | 7.88 | 6.95
64 | ПС 35/10 Амосовка | 2*2,5 | 0.31 | 0.2 | 120 | 0.11 | 0 | 2.63 | 2.52 | 2.52 | открыт
65 | ПС 35/10 Афанасьевка (ЮЭС) | 1,6+2,5 | 0.5 | 0.37 | 120 | 0.13 | 0 | 1.68 | 1.55 | 1.55 | открыт
66 | ПС 35/10 Б.Солдатское 2 | 2*4 | 1.4 | 1.1 | 80 | 0.3 | 0 | 4.2 | 3.9 | 3.9 | открыт
67 | ПС 35/10 Б.Змеинец | 2*1,6 | 0.23 | 1.43 | 120 | -1.2 | 0 | 1.68 | 2.88 | 2.88 | открыт
68 | ПС 35/10 Безлесная | 2*4 | 1.19 | 6.1 | 0 | -4.91 | 0 | 4.2 | 9.11 | 9.11 | открыт
69 | ПС 35/10 Береза | 1,0+2,5 | 0.49 | 0.15 | 120 | 0.34 | 0 | 1.05 | 0.71 | 0.71 | открыт
70 | ПС 35/10 Благодать | 2,5+4 | 0.99 | 0.29 | 120 | 0.7 | 0 | 2.63 | 1.93 | 1.93 | открыт
71 | ПС 35/10 Быканово | 2*2,5 | 0.5 | 0.41 | 120 | 0.09 | 0 | 2.63 | 2.54 | 2.54 | открыт
72 | ПС 35/10 В. Любаж | 4+10 | 1.17 | 0.4 | 120 | 0.77 | 0 | 4.2 | 3.43 | 3.43 | открыт
73 | ПС 35/10 Веселое | 2*1,6 | 0.8 | 0.22 | 120 | 0.58 | 0 | 1.68 | 1.1 | 1.1 | открыт
74 | ПС 35/10 Волобуевка | 2,5+4 | 0.57 | 0.46 | 120 | 0.11 | 0 | 2.63 | 2.52 | 2.52 | открыт
75 | ПС 35/10 Воропаево | 2*4 | 0.87 | 0 | 0 | 0.87 | 0 | 4.2 | 3.33 | 3.33 | открыт
76 | ПС 35/10 Восточная | 2*6,3 | 4.13 | 0.46 | 120 | 3.67 | 0 | 6.62 | 2.95 | 2.95 | открыт
77 | ПС 35/10 Выгорное | 2*2,5 | 1.22 | 0.51 | 120 | 0.71 | 0 | 2.63 | 1.92 | 1.92 | открыт
78 | ПС 35/10 Гастомля | 2*1,6 | 0.3 | 0.17 | 120 | 0.13 | 0 | 1.68 | 1.55 | 1.55 | открыт
79 | ПС 35/10 Городок | 2*4 | 1.6 | 0.7 | 45 | 0.9 | 0 | 4.2 | 3.3 | 3.3 | открыт
80 | ПС 35/10 Гуево | 2*2,5 | 1.2 | 1.69 | 20 | -0.49 | 0 | 2.63 | 3.12 | 3.12 | открыт
81 | ПС 35/10 Долженково | 2*1,6 | 0.4 | 0.38 | 120 | 0.02 | 0 | 1.68 | 1.66 | 1.66 | открыт
82 | ПС 35/6 Духовец | 2,5+4 | 3.33 | 3.5 | 0 | -0.17 | 0 | 2.63 | 2.8 | 2.8 | открыт
83 | ПС 35/10 Жерновец | 2*2,5 | 0.4 | 0.26 | 120 | 0.14 | 0 | 2.63 | 2.49 | 2.49 | открыт
84 | ПС 35/6 Западная | 2*10 | 12.57 | 2.5 | 0 | 10.07 | 0 | 10.5 | 0.43 | 0.43 | открыт
85 | ПС 35/10 Золотухинская КРС | 2*4 | 1.1 | 1.67 | 0 | -0.57 | 0 | 4.2 | 4.77 | 4.77 | открыт
86 | ПС 35/10 Зуевка | 1,6+2,5 | 0.9 | 0.93 | 45 | -0.03 | 0 | 1.68 | 1.71 | 1.71 | открыт
87 | ПС 35/10 Иванино | 2*6,3 | 2.19 | 2.69 | 80 | -0.5 | 0 | 6.62 | 7.12 | 7.12 | открыт
88 | ПС 35/10 Калиновка | 1,8+2,5 | 0.68 | 0.5 | 120 | 0.18 | 0 | 1.89 | 1.71 | 1.71 | открыт
89 | ПС 35/10 Кириловка | 2*1,6 | 0.29 | 0.52 | 120 | -0.23 | 0 | 1.68 | 1.91 | 1.91 | открыт
90 | ПС 35/6 Кислинская | 2*10 | 16.7 | 6.25 | 20 | 10.45 | 0 | 10.5 | 0.05 | 0.05 | открыт
91 | ПС 35/10 Комбизавод | 4+6,3 | 0.29 | 0 | 0 | 0.29 | 0 | 4.2 | 3.91 | 3.91 | открыт
92 | ПС 35/10 Комбикормовый завод | 2*6,3 | 3.31 | 0.21 | 120 | 3.1 | 0 | 6.62 | 3.52 | 3.52 | открыт
93 | ПС 35/10 Коммунальная | 3,2+4 | 2.66 | 1.14 | 80 | 1.52 | 0 | 3.36 | 1.84 | 1.84 | открыт
94 | ПС 35/10 Коренево | 4+6,3 | 3.45 | 2.7 | 80 | 0.75 | 0 | 4.2 | 3.45 | 3.45 | открыт
95 | ПС 35/10 Кремяное | 2,5+4 | 0.41 | 0.24 | 120 | 0.17 | 0 | 2.63 | 2.46 | 2.46 | открыт
96 | ПС 35/10 Крупец | 1,8+2,5 | 1.6 | 0.42 | 120 | 1.18 | 0 | 1.89 | 0.71 | 0.71 | открыт
97 | ПС 35/10 Кульбаки | 2*2,5 | 0.88 | 0.6 | 120 | 0.28 | 0 | 2.63 | 2.35 | 2.35 | открыт
98 | ПС 35/10 Культпросвет | 2*2,5 | 0.18 | 0.17 | 120 | 0.01 | 0 | 2.63 | 2.62 | 2.62 | открыт
99 | ПС 35/10 Курчатов | 2*10 | 4.85 | 4.5 | 80 | 0.35 | 0 | 10.5 | 10.15 | 10.15 | открыт
100 | ПС 35/10 Куток | 2*2,5 | 0.17 | 0.05 | 120 | 0.12 | 0 | 2.63 | 2.51 | 2.51 | открыт
101 | ПС 35/10 Линец | 2*2,5 | 0.67 | 0.25 | 120 | 0.42 | 0 | 2.63 | 2.21 | 2.21 | открыт
102 | ПС 35/10 Луч | 2*6,3 | 2.83 | 0.23 | 120 | 2.6 | 0 | 6.62 | 4.02 | 4.02 | открыт
103 | ПС 35/10 Любимовка-2 | 2*4 | 0.75 | 1.59 | 80 | -0.84 | 0 | 4.2 | 5.04 | 5.04 | открыт
104 | ПС 35/10 Матвеевка | 2*2,5 | 0.67 | 0.08 | 120 | 0.59 | 0 | 2.63 | 2.04 | 2.04 | открыт
105 | ПС 35/10 Маяк | 2*2,5 | 0.41 | 0.3 | 120 | 0.11 | 0 | 2.63 | 2.52 | 2.52 | открыт
106 | ПС 35/10 Михайловка | 4+6,3 | 2.15 | 1.7 | 80 | 0.45 | 0 | 4.2 | 3.75 | 3.75 | открыт
107 | ПС 35/10 Мурыновка | 2*4 | 0.63 | 0.3 | 120 | 0.33 | 0 | 4.2 | 3.87 | 3.87 | открыт
108 | ПС 35/10 Н. Борки | 2*2,5 | 0.5 | 0.63 | 120 | -0.13 | 0 | 2.63 | 2.76 | 2.76 | открыт
109 | ПС 35/10 Никольская | 1,6+1,8 | 0.36 | 0.03 | 80 | 0.33 | 0 | 1.68 | 1.35 | 1.35 | открыт
110 | ПС 35/10 Новая | 2*2,5 | 1.08 | 0.4 | 120 | 0.68 | 0 | 2.63 | 1.95 | 1.95 | открыт
111 | ПС 35/10 Орехово | 2*2,5 | 0.73 | 0.19 | 120 | 0.54 | 0 | 2.63 | 2.09 | 2.09 | открыт
112 | ПС 35/10 Орловка | 2*2,5 | 0.17 | 0.52 | 120 | -0.35 | 0 | 2.63 | 2.98 | 2.98 | открыт
113 | ПС 35/10 Осоцкое | 2*2,5 | 0.19 | 0.2 | 120 | -0.01 | 0 | 2.63 | 2.64 | 2.64 | открыт
114 | ПС 35/10 Охочевка | 4+6,3 | 1.27 | 0.74 | 120 | 0.53 | 0 | 4.2 | 3.67 | 3.67 | открыт
115 | ПС 35/10 Панино | 2*2,5 | 0.26 | 0.11 | 80 | 0.15 | 0 | 2.63 | 2.48 | 2.48 | открыт
116 | ПС 35/10 Первоавгустовка | 2,5+3,2 | 0.74 | 0.52 | 120 | 0.22 | 0 | 2.63 | 2.41 | 2.41 | открыт
117 | ПС 35/10 Петринка | 2,5+4 | 1.1 | 0.3 | 120 | 0.8 | 0 | 2.63 | 1.83 | 1.83 | открыт
118 | ПС 35/10 Платава | 2*2,5 | 1.07 | 0.26 | 120 | 0.81 | 0 | 2.63 | 1.82 | 1.82 | открыт
119 | ПС 35/10 Погожее | 2*1,6 | 0.23 | 0.46 | 120 | -0.23 | 0 | 1.68 | 1.91 | 1.91 | открыт
120 | ПС 35/10 Поречное | 2*4 | 0.5 | 1.16 | 120 | -0.66 | 0 | 4.2 | 4.86 | 4.86 | открыт
121 | ПС 35/10 Почепное | 2*6,3 | 0.13 | 0.08 | 120 | 0.05 | 0 | 6.62 | 6.57 | 6.57 | открыт
122 | ПС 35/10 Пригородная | 2*2,5 | 0.52 | 0.3 | 80 | 0.22 | 0 | 2.63 | 2.41 | 2.41 | открыт
123 | ПС 35/10 Пселец | 2*1,6 | 0.2 | 0.24 | 120 | -0.04 | 0 | 1.68 | 1.72 | 1.72 | открыт
124 | ПС 35/10 Пузачи | 1,6+4 | 0.4 | 0.43 | 120 | -0.03 | 0 | 1.68 | 1.71 | 1.71 | открыт
125 | ПС 35/10 Пушкарное | 2*2,5 | 0.8 | 0.32 | 120 | 0.48 | 0 | 2.625 | 2.145 | 2.145 | открыт
126 | ПС 35/10 Р.Колодец | 2*2,5 | 0.6 | 0.44 | 120 | 0.16 | 0 | 2.625 | 2.465 | 2.465 | открыт
127 | ПС 35/10 Разветье | 2*4 | 2.38 | 1.03 | 120 | 1.35 | 0 | 4.2 | 2.85 | 2.85 | открыт
128 | ПС 35/10 В. Реутец | 2*4 | 0.28 | 0.11 | 120 | 0.17 | 0 | 4.2 | 4.03 | 4.03 | открыт
129 | ПС 35/10 Рождественка | 2*1,6 | 0.3 | 0.29 | 120 | 0.01 | 0 | 1.68 | 1.67 | 1.67 | открыт
130 | ПС 35/10 Рубильник | 2*2,5 | 0.78 | 1.18 | 80 | -0.4 | 0 | 2.625 | 3.025 | 3.025 | открыт
131 | ПС 35/10 Рыжково | 2*1,6 | 0.23 | 0.08 | 20 | 0.15 | 0 | 1.68 | 1.53 | 1.53 | открыт
132 | ПС 35/10 Сапогово | 2*2,5 | 1.57 | 0.6 | 20 | 0.97 | 0 | 2.63 | 1.66 | 1.66 | открыт
133 | ПС 35/10 Свобода-сельская | 2*6,3 | 4.01 | 2.25 | 80 | 1.76 | 0 | 6.615 | 4.855 | 4.855 | открыт
134 | ПС 35/10 Селекционная | 2*4 | 1.56 | 1.4 | 45 | 0.16 | 0 | 4.2 | 4.04 | 4.04 | открыт
135 | ПС 35/10 Семеновка | 2*2,5 | 0.5 | 0 | - | 0.5 | 0 | 2.625 | 2.125 | 2.125 | открыт
136 | ПС 35/10 Семзавод | 2*2,5 | 0.6 | 0.6 | 120 | 0 | 0 | 2.63 | 2.63 | 2.63 | открыт
137 | ПС 35/10 Снагость | 2*4 | 1.26 | 0.05 | 10 | 1.21 | 0 | 4.2 | 2.99 | 2.99 | открыт
138 | ПС 35/10 СОМ | 1,6+4 | 1.56 | 0.08 | 10 | 1.48 | 0 | 1.68 | 0.2 | 0.2 | открыт
139 | ПС 35/10 Сосновый Бор | 3,2+4 | 0.69 | 0.69 | 120 | 0 | 0 | 3.36 | 3.36 | 3.36 | открыт
140 | ПС 35/10 Стаканово | 2*2,5 | 1.23 | 0.58 | 80 | 0.65 | 0 | 2.625 | 1.975 | 1.975 | открыт
141 | ПС 35/10 Старково | 2*1,6 | 0.43 | 0.2 | 80 | 0.23 | 0 | 1.68 | 1.45 | 1.45 | открыт
142 | ПС 35/10 Старшее | 2*1,6 | 0.31 | 0.2 | 120 | 0.11 | 0 | 1.68 | 1.57 | 1.57 | открыт
143 | ПС 35/10 Теплицы | 2*4 | 2.25 | 1.08 | 45 | 1.17 | 0 | 4.2 | 3.03 | 3.03 | открыт
144 | ПС 35/10 Туровка | 2*2,5 | 0.8 | 0.6 | 120 | 0.2 | 0 | 2.63 | 2.43 | 2.43 | открыт
145 | ПС 35/10 Успенка | 2*2,5 | 1.19 | 1 | 80 | 0.19 | 0 | 2.63 | 2.44 | 2.44 | открыт
146 | ПС 35/6 Центральная | 2*25 | 24.9 | 5 | 10 | 19.9 | 0 | 26.25 | 6.35 | 6.35 | открыт
147 | ПС 35/10 Чермошное | 2*2,5 | 0.4 | 0.5 | 120 | -0.1 | 0 | 4.2 | 4.3 | 4.3 | открыт
148 | ПС 35/10 Шаталовка | 2,5+4 | 0.31 | 0.21 | 80 | 0.1 | 0 | 2.625 | 2.525 | 2.525 | открыт
149 | ПС 35/10 Шипы | 2*2,5 | 0.2 | 0.3 | 120 | -0.1 | 0 | 2.625 | 2.725 | 2.725 | открыт
150 | ПС 35/10 Элеватор | 4+6,3 | 2.21 | 0.6 | 120 | 1.61 | 0 | 4.2 | 2.59 | 2.59 | открыт
151 | ПС 35/10 Юго-Западная | 2*10 | 9.28 | 4.7 | 80 | 4.58 | 0 | 10.5 | 5.92 | 5.92 | открыт
152 | ПС 35/10 ЖБИ | 2*2,5 | 1.97 | 3.9 | 120 | -1.93 | 0 | 2.625 | 4.555 | 4.555 | открыт
| ИТОГО: | 3185.9 | 763.705 | 777.41 | [5 empty] | 1191.575
| дефицит | [8 empty] | -8.27
| профицит | [8 empty] | 1183.31
*Примечание: Дефицит мощности по ПС Высокая обусловлен переводом нагрузок с ПС Центральная и будет снят после ввода в эксплуатацию
РУ-10 кВ на ПС Центральная.
Зам.директора по техническим вопросам -
|  | Главный инженер | [6 empty] | А.Н. Рудневский

## Ожидаемый дефицит, табл. 2
Приложение 2
Форма расчёта пропускной способности Центров питания филиала ОАО "МРСК Центра" -"Курскэнерго" за май 2010 г. по итогам зимнего замера максимума нагрузки 16.12.2009 г.
таблица 2
№п/п | Наименование объекта центра питания, класс напряжения | Ожидаемый дефицит/профицит | [9 empty] | примечание
|  | Установленная мощность трансформаторов Sуст. с указанием их количества, шт/ МВА | Дополнительная мощность по выданным ТУ | Ожидаемая нагрузка на ЦП | Полная мощность, перераспределяемая в соответствии с ПТЭ, МВА за время |  | Полная мощность с учётом перераспределения, МВА | Ограничивающие факторы, МВА | Допустимая нагрузка расчётная в режиме n-1, МВА | Дефицит /профицит ЦП, МВА
[5 empty] | МВА | Мин.
1 | 2 | 3 |  | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
Однотрансформаторные ПС
1 | ПС 110/35/10 Артюховка | 1*6,3 | 0.016 | 1.656 | 6.3 | 1 сутки | 6.3 | 0 | 6.3 | 4.644 | 1.189 | открыт
| Ном. Мощность СН, МВА | 6.3 | 0.011 | 1.111 | 2.3 | 1 сутки | 2.3 | 0 | 2.3 | 1.189
| Ном. Мощность НН, МВА | 6.3 | 0.005 | 0.545 | 4 | 1 сутки | 4 | 0 | 4 | 3.455
2 | ПС 110/10 Бекетово | 1*6,3 |  | 0.39 | 2.15 | 1 сутки | 2.15 | 0 | 2.15 | 1.76 | 1.76 | открыт
3 | ПС 110/35/10 Беседино | 1*6,3 | 0.181 | 3.021 | 6.7 | 1 сутки | 6.7 | 0 | 6.7 | 3.679 | 0.012 | открыт
| Ном. Мощность СН, МВА | 6.3 | 0.033 | 0.533 | 4.2 | 1 сутки | 4.2 | 0 | 4.2 | 3.667
| Ном. Мощность НН, МВА | 6.3 | 0.148 | 2.488 | 2.5 | 1 сутки | 2.5 | 0 | 2.5 | 0.012
4 | ПС 110/10 Восход | 1*10,0 | 0.049 | 0.849 | 2.5 | 1 сутки | 2.5 | 0 | 2.5 | 1.651 | 1.651 | открыт
5 | ПС 110/35/10 Журятино | 1*6,3 | 0 | 0.82 | 6 | 1 сутки | 6 | 0 | 6 | 5.18 | 1.48 | открыт
| Ном. Мощность СН, МВА | 6.3 | 0 | 0 | 3.7 | 1 сутки | 3.7 | 0 | 3.7 | 3.7
| Ном. Мощность НН, МВА | 6.3 |  | 0.82 | 2.3 | 1 сутки | 2.3 | 0 | 2.3 | 1.48
6 | ПС 110/35/10 Жуковка | 1*10,0 | 0.021 | 1.121 | 5.16 | 120 | 5.16 | 0 | 5.16 | 4.039 | 0.49 | открыт
| Ном. Мощность СН, МВА | 10 | 0.021 | 0.951 | 4.5 | 1 сутки | 4.5 | 0 | 4.5 | 3.549
| Ном. Мощность НН, МВА | 10 |  | 0.17 | 0.66 | 120 | 0.66 | 0 | 0.66 | 0.49
7 | ПС 110/10 Забелье | 1*2,5 | 0.013 | 0.323 | 2.15 | 1 сутки | 2.15 | 0 | 2.15 | 1.827 | 1.827 | открыт
8 | ПС 110/10 Ивница | 1*6,3 |  | 0.4 | 0.45 | 1 сутки | 0.45 | 0 | 0.45 | 0.05 | 0.05 | открыт
9 | ПС 110/35/10 Лачиново | 1*10,0 | 0.46 | 1.74 | 5.13 | 1 сутки | 5.13 | 0 | 5.13 | 3.39 | 0.54 | открыт
| Ном. Мощность СН, МВА | 10 | 0 | 0.75 | 3.6 | 1 сутки | 3.6 | 0 | 3.6 | 2.85
| Ном. Мощность НН, МВА | 10 | 0.46 | 0.99 | 1.53 | 1 сутки | 1.53 | 0 | 1.53 | 0.54
10 | ПС 110/10 Малая Локня | 1*10,0 |  | 1.2 | 1.21 | 1 сутки | 1.21 | 0 | 1.21 | 0.01 | 0.01 | открыт
11 | ПС 110/35/10 Марица | 1*2,5 | 0.01 | 1 | 1.92 | 1 сутки | 1.92 | 0 | 1.92 | 0.92 | 0.92 | открыт
12 | ПС 110/35/10 Расховец | 1 х 6,3 | 0.014 | 0.574 | 5.89 | 1 сутки | 5.89 | 0 | 5.89 | 5.316 | 1.97 | открыт
| Ном. Мощность СН, МВА | 6.3 | 0.014 | 0.394 | 3.74 | 1 сутки | 3.74 | 0 | 3.74 | 3.346
| Ном. Мощность НН, МВА | 6.3 |  | 0.18 | 2.15 | 1 сутки | 2.15 | 0 | 2.15 | 1.97
13 | ПС 110/10 Семеновская | 1 х 2,5 | 0.003 | 0.403 | 1.4 | 1 сутки | 1.4 | 0 | 1.4 | 0.997 | 0.997 | открыт
14 | ПС 110/6 Тепличная | 1 х 16,0 | 5.7 | 9.8 | 6.64 | 1 сутки | 6.64 | 0 | 6.64 | -3.16 | -3.16 | закрыт
15 | ПС 110/35/10 Троицкая | 1 х 10,0 | 0.77 | 3.78 | 7.5 | 1 сутки | 7.5 | 0 | 7.5 | 3.72 | 0.773 | открыт
| Ном. Мощность СН, МВА | 10 | 0.753 | 3.453 | 6.4 | 1 сутки | 6.4 | 0 | 6.4 | 2.947
| Ном. Мощность НН, МВА | 10 | 0.017 | 0.327 | 1.1 | 1 сутки | 1.1 | 0 | 1.1 | 0.773
16 | ПС 35/10 Автодор | 1 х 2,5 | 0.043 | 0.503 | 0.8 | 1 сутки | 0.8 | 0 | 0.8 | 0.297 | 0.297 | открыт
17 | ПС 35/10 Агроном | 1 х 1,8 | 0.195 | 0.895 | 0.96 | 1 сутки | 0.96 | 0 | 0.96 | 0.065 | 0.065 | открыт
18 | ПС 35/10 Акимовка | 1 х 2,5 |  | 0.25 | 0.68 | 1 сутки | 0.68 | 0 | 0.68 | 0.43 | 0.43 | открыт
19 | ПС 35/10 Алексеевка | 1 х 2,5 | 0.015 | 0.295 | 1.43 | 1 сутки | 1.43 | 0 | 1.43 | 1.135 | 1.135 | открыт
20 | ПС 35/10 Афанасьевка (ЗЭС) | 1 х 4,0 | 0.015 | 0.565 | 1.34 | 1 сутки | 1.34 | 0 | 1.34 | 0.775 | 0.775 | открыт
21 | ПС 35/10 Б. Гнеушево | 1 х 2,5 |  | 0.77 | 0.96 | 1 сутки | 0.96 | 0 | 0.96 | 0.19 | 0.19 | открыт
22 | ПС 35/10 Б.Солдатское 1 | 1 х 3,2 | 0.231 | 1.011 | 2.83 | 1 сутки | 2.83 | 0 | 2.83 | 1.819 | 1.819 | открыт
23 | ПС 35/10 Банищи | 1 х 1,6 | 0.015 | 0.235 | 0.64 | 1 сутки | 0.64 | 0 | 0.64 | 0.405 | 0.405 | открыт
24 | ПС 35/10 Бараново | 1 х 4,0 | 0.0977 | 0.5577 | 1.43 | 1 сутки | 1.43 | 0 | 1.43 | 0.8723 | 0.8723 | открыт
25 | ПС 35/10 Белгородка | 1 х 2,5 | 0.015 | 0.285 | 2.15 | 1 сутки | 2.15 | 0 | 2.15 | 1.865 | 1.865 | открыт
26 | ПС 35/10 Белица | 1 х 4,0 | 0.262 | 0.862 | 1.76 | 1 сутки | 1.76 | 0 | 1.76 | 0.898 | 0.898 | открыт
27 | ПС 35/10 Бирюковка | 1х1,6 |  | 0.6 | 0.67 | 1 сутки | 0.67 | 0 | 0.67 | 0.07 | 0.07 | открыт
28 | ПС 35/10 Бобровка | 1 х 1,6 |  | 0.24 | 0.67 | 1 сутки | 0.67 | 0 | 0.67 | 0.43 | 0.43 | открыт
29 | ПС 35/10 Боброво | 1 х 2,5 |  | 0.42 | 0.76 | 1 сутки | 0.76 | 0 | 0.76 | 0.34 | 0.34 | открыт
30 | ПС 35/10 Будки | 1 х 1,0 |  | 0.09 | 0.64 | 1 сутки | 0.64 | 0 | 0.64 | 0.55 | 0.55 | открыт
31 | ПС 35/10 Букреевка (ЦЭС) | 1 х 1,8 | 0.037 | 0.627 | 1.6 | 50 | 1.6 | 0 | 1.6 | 0.973 | 0.973 | открыт
32 | ПС 35/10 Букреевка (ЗЭС) | 1 х 1,6 | 0.037 | 0.247 | 0.64 | 1 сутки | 0.64 | 0 | 0.64 | 0.393 | 0.393 | открыт
33 | ПС 35/10 Бурцевка | 1 х 1,6 | 0.022 | 0.202 | 1.43 | 1 сутки | 1.43 | 0 | 1.43 | 1.228 | 1.228 | открыт
34 | ПС 35/10 Быково | 1 х 4,0 | 0.205 | 1.095 | 1.43 | 1 сутки | 1.43 | 0 | 1.43 | 0.335 | 0.335 | открыт
35 | ПС 35/10 В. Щигор | 1 х 2,5 |  | 0.12 | 2.15 | 1 сутки | 2.15 | 0 | 2.15 | 2.03 | 2.03 | открыт
36 | ПС 35/10 Ванино | 1 х 2,5 | 0.065 | 0.425 | 0.8 | 1 сутки | 0.8 | 0 | 0.8 | 0.375 | 0.375 | открыт
37 | ПС 35/10 Васильевка | 1 х 2,5 | 0.035 | 0.675 | 1.05 | 1 сутки | 1.05 | 0 | 1.05 | 0.375 | 0.375 | открыт
38 | ПС 35/10 Водохранилище | 1 х 4,0 | 3.54 | 5.12 | 2.72 | 1 сутки | 2.72 | 0 | 2.72 | -2.4 | -2.4 | закрыт
39 | ПС 35/10 Волоконск | 1 х 2,5 |  | 0.3 | 1.1 | 1 сутки | 1.1 | 0 | 1.1 | 0.8 | 0.8 | открыт
40 | ПС 35/10 Воробьевка | 1 х 2,5 | 0.014 | 0.664 | 0.9 | 1 сутки | 0.9 | 0 | 0.9 | 0.236 | 0.236 | открыт
41 | ПС 35/10 Воронок | 1 х 4,0 | 0.013 | 0.873 | 2.1 | 1 сутки | 2.1 | 0 | 2.1 | 1.227 | 1.227 | открыт
42 | ПС 35/10 Вязовое | 1 х 2,5 |  | 0.66 | 2.15 | 1 сутки | 2.15 | 0 | 2.15 | 1.49 | 1.49 | открыт
43 | ПС 35/10 Гахово | 1 х 2,5 | 0.02 | 0.23 | 1.8 | 1 сутки | 1.8 | 0 | 1.8 | 1.57 | 1.57 | открыт
44 | ПС 35/10 Генеральшино | 1 х 2,5 | 0.01 | 0.26 | 1.5 | 1 сутки | 1.5 | 0 | 1.5 | 1.24 | 1.24 | открыт
45 | ПС 35/10 Глазово | 1 х 2,5 | 0.02 | 0.96 | 1.4 | 1 сутки | 1.4 | 0 | 1.4 | 0.44 | 0.44 | открыт
46 | ПС 35/10 Глебово | 1 х 2,5 | 0.018 | 0.508 | 1.4 | 1 сутки | 1.4 | 0 | 1.4 | 0.892 | 0.892 | открыт
47 | ПС 35/10 Гордеевка | 1 х 1,6 | 0.02 | 0.14 | 0.7 | 1 сутки | 0.7 | 0 | 0.7 | 0.56 | 0.56 | открыт
48 | ПС 35/10 Городенск | 1 х 1,6 | 0.044 | 0.634 | 0.76 | 1 сутки | 0.76 | 0 | 0.76 | 0.126 | 0.126 | открыт
49 | ПС 35/10 Горяйново | 1 х 2,5 | 0.011 | 0.511 | 1.1 | 1 сутки | 1.1 | 0 | 1.1 | 0.589 | 0.589 | открыт
50 | ПС 35/10 12-й Госконезавод | 1 х 2,5 |  | 0.53 | 1.43 | 1 сутки | 1.43 | 0 | 1.43 | 0.9 | 0.9 | открыт
51 | ПС 35/10 Грайворонка | 1 х 2,5 | 0.042 | 0.542 | 1.43 | 1 сутки | 1.43 | 0 | 1.43 | 0.888 | 0.888 | открыт
52 | ПС 35/10 Гриневка | 1 х 2,5 | 0.014 | 0.294 | 2.85 | 1 сутки | 2.85 | 0 | 2.85 | 2.556 | 2.556 | открыт
53 | ПС 35/10 Густомой | 1 х 1,6 | 0.006 | 0.216 | 0.94 | 1 сутки | 0.94 | 0 | 0.94 | 0.724 | 0.724 | открыт
54 | ПС 35/10 Дарьино | 1 х 2,5 | 0.032 | 0.432 | 1.8 | 1 сутки | 1.8 | 0 | 1.8 | 1.368 | 1.368 | открыт
55 | ПС 35/10 Демякино | 1 х 2,5 | 0.036 | 0.466 | 0.8 | 1 сутки | 0.8 | 0 | 0.8 | 0.334 | 0.334 | открыт
56 | ПС 35/10 Ефросимовка | 1 х 1,8 | 0.025 | 0.405 | 1.07 | 1 сутки | 1.07 | 0 | 1.07 | 0.665 | 0.665 | открыт
57 | ПС 35/10 Жданово | 1 х 2,5 | 0.038 | 0.418 | 0.85 | 1 сутки | 0.85 | 0 | 0.85 | 0.432 | 0.432 | открыт
58 | ПС 35/10 Защитное | 1 х 1,6 | 0.011 | 0.331 | 2.15 | 1 сутки | 2.15 | 0 | 2.15 | 1.819 | 1.819 | открыт
59 | ПС 35/10 Званное | 1 х 2,5 | 0.043 | 0.643 | 0.84 | 1 сутки | 0.84 | 0 | 0.84 | 0.197 | 0.197 | открыт
60 | ПС 35/10 Знаменка | 1 х 1,8 |  | 1.01 | 2.15 | 1 сутки | 2.15 | 0 | 2.15 | 1.14 | 1.14 | открыт
61 | ПС 35/10 Искра | 1 х 2,5 | 0.033 | 0.193 | 0.58 | 1 сутки | 0.58 | 0 | 0.58 | 0.387 | 0.387 | открыт
62 | ПС 35/10 Казанка | 1 х 4,0 | 0.006 | 0.336 | 0.8 | 1 сутки | 0.8 | 0 | 0.8 | 0.464 | 0.464 | открыт
63 | ПС 35/10 Калиновка (новая) | 1 х 2,5 | 0.01 | 0.18 | 1.8 | 1 сутки | 1.8 | 0 | 1.8 | 1.62 | 1.62 | открыт
64 | ПС 35/10 Карыж | 1 х 1,6 | 0.01 | 0.19 | 0.64 | 1 сутки | 0.64 | 0 | 0.64 | 0.45 | 0.45 | открыт
65 | ПС 35/10 Китаевка | 1 х 1,6 | 0.207 | 0.467 | 0.74 | 1 сутки | 0.74 | 0 | 0.74 | 0.273 | 0.273 | открыт
66 | ПС 35/10 Кобылки | 1 х 2,5 | 0.031 | 0.711 | 1.53 | 1 сутки | 1.53 | 0 | 1.53 | 0.819 | 0.819 | открыт
67 | ПС 35/10 Колонтаевка | 1 х 2,5 |  | 0.26 | 0.84 | 1 сутки | 0.84 | 0 | 0.84 | 0.58 | 0.58 | открыт
68 | ПС 35/10 Кондратовка | 1 х 1,8 | 0.024 | 0.574 | 1.42 | 1 сутки | 1.42 | 0 | 1.42 | 0.846 | 0.846 | открыт
69 | ПС 35/10 Коровяковка | 1 х 1,6 | 0.017 | 0.227 | 0.76 | 1 сутки | 0.76 | 0 | 0.76 | 0.533 | 0.533 | открыт
70 | ПС 35/10 Леженьки | 1 х 2,5 | 0.014 | 0.104 | 1.43 | 1 сутки | 1.43 | 0 | 1.43 | 1.326 | 1.326 | открыт
71 | ПС 35/10 Ленинская | 1 х 1,8 | 0.035 | 0.705 | 0.73 | 1 сутки | 0.73 | 0 | 0.73 | 0.025 | 0.025 | открыт
72 | ПС 35/10 Лобазовка | 1 х 2,5 | 0.011 | 0.871 | 1.09 | 1 сутки | 1.09 | 0 | 1.09 | 0.219 | 0.219 | открыт
73 | ПС 35/10 Луговка | 1 х 1,6 | 0.035 | 0.575 | 1.29 | 1 сутки | 1.29 | 0 | 1.29 | 0.715 | 0.715 | открыт
74 | ПС 35/10 Любава | 1 х 6,3 | 0.008 | 0.318 | 1.15 | 1 сутки | 1.15 | 0 | 1.15 | 0.832 | 0.832 | открыт
75 | ПС 35/10 Любимовка-1 | 1 х 3,2 | 0.041 | 0.041 | 0.96 | 1 сутки | 0.96 | 0 | 0.96 | 0.919 | 0.919 | открыт
76 | ПС 35/10 М. Каменец | 1 х 1,6 | 0.051 | 0.651 | 1.1 | 1 сутки | 1.1 | 0 | 1.1 | 0.449 | 0.449 | открыт
77 | ПС 35/10 М. Гнеушево | 1 х 4,0 | 0.015 | 0.715 | 1.28 | 1 сутки | 1.28 | 0 | 1.28 | 0.565 | 0.565 | открыт
78 | ПС 35/10 М. Крюки | 1 х 2,5 | 0.01 | 0.41 | 1.19 | 1 сутки | 1.19 | 0 | 1.19 | 0.78 | 0.78 | открыт
79 | ПС 35/10 Марково | 1 х 2,5 | 0.01 | 0.66 | 0.8 | 1 сутки | 0.8 | 0 | 0.8 | 0.14 | 0.14 | открыт
80 | ПС 35/10 Мармыжи | 1 х 2,5 |  | 0.21 | 1.33 | 1 сутки | 1.33 | 0 | 1.33 | 1.12 | 1.12 | открыт
81 | ПС 35/10 Меловое | 1 х 4,0 | 0.013 | 1.003 | 2.15 | 1 сутки | 2.15 | 0 | 2.15 | 1.147 | 1.147 | открыт
82 | ПС 35/10 Моква | 1 х 4,0 | 0.057 | 0.557 | 2.15 | 1 сутки | 2.15 | 0 | 2.15 | 1.593 | 1.593 | открыт
83 | ПС 35/10 Мокрушино | 1 х 1,6 | 0.026 | 0.626 | 1.1 | 1 сутки | 1.1 | 0 | 1.1 | 0.474 | 0.474 | открыт
84 | ПС 35/10 Молотычи | 1 х 2,5 |  | 0.4 | 0.9 | 1 сутки | 0.9 | 0 | 0.9 | 0.5 | 0.5 | открыт
85 | ПС 35/10 Мочаки | 1 х 2,5 |  | 0.03 | 1.07 | 1 сутки | 1.07 | 0 | 1.07 | 1.04 | 1.04 | открыт
86 | ПС 35/10 Н. Владимировка | 1 х 2,5 |  | 0.08 | 4.3 | 1 сутки | 4.3 | 0 | 4.3 | 4.22 | 4.22 | открыт
87 | ПС 35/10 Н. Гурово | 1 х 4,0 | 0.008 | 0.738 | 2.15 | 1 сутки | 2.15 | 0 | 2.15 | 1.412 | 1.412 | открыт
88 | ПС 35/10 Надейка | 1 х 2,5 | 0.008 | 0.168 | 1.4 | 1 сутки | 1.4 | 0 | 1.4 | 1.232 | 1.232 | открыт
89 | ПС 35/10 Нива | 1 х 2,5 | 0.015 | 0.415 | 1.56 | 1 сутки | 1.56 | 0 | 1.56 | 1.145 | 1.145 | открыт
90 | ПС 35/10 Ольговка | 1 х 2,5 | 0.032 | 0.442 | 0.97 | 1 сутки | 0.97 | 0 | 0.97 | 0.528 | 0.528 | открыт
91 | ПС 35/10 Ольховатка | 1 х 4,0 | 0.01 | 0.39 | 0.64 | 1 сутки | 0.64 | 0 | 0.64 | 0.25 | 0.25 | открыт
92 | ПС 35/10 Оросительная | 1 х 4,0 | 0.783 | 1.713 | 2.97 | 1 сутки | 2.97 | 0 | 2.97 | 1.257 | 1.257 | открыт
93 | ПС 35/10 Пены-2 | 1 х 2,5 | 0.41 | 1.01 | 2.32 | 1 сутки | 2.32 | 0 | 2.32 | 1.31 | 1.31 | открыт
94 | ПС 35/10 Переступлино (стар) | 1 х 2,5 |  | 0.16 | 1.4 | 1 сутки | 1.4 | 0 | 1.4 | 1.24 | 1.24 | открыт
95 | ПС 35/10 Переступлино (нов) | 1 х 2,5 |  | 0.36 | 1.4 | 1 сутки | 1.4 | 0 | 1.4 | 1.04 | 1.04 | открыт
96 | ПС 35/10 Петрово | 1 х 6,3 | 0.099 | 1.099 | 2.15 | 1 сутки | 2.15 | 0 | 2.15 | 1.051 | 1.051 | открыт
97 | ПС 35/10 Петровская | 1 х 2,5 |  | 0.03 | 0.74 | 1 сутки | 0.74 | 0 | 0.74 | 0.71 | 0.71 | открыт
98 | ПС 35/10 Покровское | 1 х 2,5 | 0.015 | 0.285 | 2.15 | 1 сутки | 2.15 | 0 | 2.15 | 1.865 | 1.865 | открыт
99 | ПС 35/10 Прилепы | 1 х 1,6 | 0.009 | 0.539 | 2.15 | 1 сутки | 2.15 | 0 | 2.15 | 1.611 | 1.611 | открыт
100 | ПС 35/10 Пристень | 1 х 4,0 | 0.047 | 2.347 | 3.3 | 1 сутки | 3.3 | 0 | 3.3 | 0.953 | 0.953 | открыт
101 | ПС 35/10 Р. Буды 35/10 | 1 х 4,0 | 0.012 | 0.012 | 0.74 | 1 сутки | 0.74 | 0 | 0.74 | 0.728 | 0.728 | открыт
102 | ПС 35/10 Реут | 1 х 2,5 |  | 0.16 | 0.86 | 0 | 0.86 | 0 | 0.86 | 0.7 | 0.7 | открыт
103 | ПС 35/10 Ровенка | 1 х 1,6 | 0.015 | 0.175 | 1.43 | 1 сутки | 1.43 | 0 | 1.43 | 1.255 | 1.255 | открыт
104 | ПС 35/10 Родина (СЭС) | 1 х 2,5 | 0.033 | 0.203 | 0.7 | 1 сутки | 0.7 | 0 | 0.7 | 0.497 | 0.497 | открыт
105 | ПС 35/10 Родина (ВЭС) | 1 х 4,0 |  | 0.5 | 2.3 | 1 сутки | 2.3 | 0 | 2.3 | 1.8 | 1.8 | открыт
106 | ПС 35/10 Рубанщина | 1 х 2,5 | 0.003 | 0.403 | 1.31 | 1 сутки | 1.31 | 0 | 1.31 | 0.907 | 0.907 | открыт
107 | ПС 35/10 Русаново | 1 х 1,8 | 0.024 | 0.414 | 1.43 | 1 сутки | 1.43 | 0 | 1.43 | 1.016 | 1.016 | открыт
108 | ПС 35/10 Рышково | 1 х 2,5 | 0.038 | 0.598 | 0.94 | 1 сутки | 0.94 | 0 | 0.94 | 0.342 | 0.342 | открыт
109 | ПС 35/10 Рязаново | 1 х 1,6 | 0.009 | 0.589 | 1.15 | 1 сутки | 1.15 | 0 | 1.15 | 0.561 | 0.561 | открыт
110 | ПС 35/10 Сазановка | 1 х 2,5 |  | 0.3 | 1.25 | 1 сутки | 1.25 | 0 | 1.25 | 0.95 | 0.95 | открыт
111 | ПС 35/10 Сергиевка | 1 х 2,5 | 0.005 | 0.405 | 2.7 | 1 сутки | 2.7 | 0 | 2.7 | 2.295 | 2.295 | открыт
112 | ПС 35/10 Соколье | 1 х 2,5 | 0.051 | 0.351 | 1.43 | 1 сутки | 1.43 | 0 | 1.43 | 1.079 | 1.079 | открыт
113 | ПС 35/10 Солнцево | 1 х 2,5 | 0.09 | 0.99 | 1.76 | 1 сутки | 1.76 | 0 | 1.76 | 0.77 | 0.77 | открыт
114 | ПС 35/10 Спасское | 1 х 1,6 |  | 0.22 | 1.1 | 1 сутки | 1.1 | 0 | 1.1 | 0.88 | 0.88 | открыт
115 | ПС 35/10 Ср. Ольшанка | 1 х 2,5 | 0.004 | 0.304 | 1.4 | 1 сутки | 1.4 | 0 | 1.4 | 1.096 | 1.096 | открыт
116 | ПС 35/10 Стрелецкая | 1 х 2,5 | 0.038 | 0.388 | 1.3 | 1 сутки | 1.3 | 0 | 1.3 | 0.912 | 0.912 | открыт
117 | ПС 35/10 Субботино | 1 х 2,5 | 0.005 | 0.605 | 1.34 | 1 сутки | 1.34 | 0 | 1.34 | 0.735 | 0.735 | открыт
118 | ПС 35/10 Сухая | 1 х 1,6 | 0.002 | 0.442 | 0.71 | 1 сутки | 0.71 | 0 | 0.71 | 0.268 | 0.268 | открыт
119 | ПС 35/10 Тельмана | 1 х 2,5 | 0.009 | 0.309 | 1.15 | 1 сутки | 1.15 | 0 | 1.15 | 0.841 | 0.841 | открыт
120 | ПС 35/10 Теребуж | 1 х 2,5 | 0.021 | 0.481 | 1.43 | 1 сутки | 1.43 | 0 | 1.43 | 0.949 | 0.949 | открыт
121 | ПС 35/10 Фатеевка | 1 х 2,5 |  | 0.08 | 0.7 | 1 сутки | 0.7 | 0 | 0.7 | 0.62 | 0.62 | открыт
122 | ПС 35/10 Фентисово | 1 х 1,6 | 0.017 | 0.187 | 1.72 | 1 сутки | 1.72 | 0 | 1.72 | 1.533 | 1.533 | открыт
123 | ПС 35/10 Чапаевская | 1 х 2,5 | 0.014 | 0.214 | 1.1 | 1 сутки | 1.1 | 0 | 1.1 | 0.886 | 0.886 | открыт
124 | ПС 35/10 Чемерки | 1 х 1,6 |  | 0.06 | 0.85 | 1 сутки | 0.85 | 0 | 0.85 | 0.79 | 0.79 | открыт
125 | ПС 35/10 Чижовка | 1 х 1,6 | 0.033 | 0.383 | 1.43 | 1 сутки | 1.43 | 0 | 1.43 | 1.047 | 1.047 | открыт
126 | ПС 35/10 Шатиловка | 1 х 2,5 | 0.011 | 0.171 | 1.43 | 1 сутки | 1.43 | 0 | 1.43 | 1.259 | 1.259 | открыт
127 | ПС 35/10 Шептуховка | 1 х 2,5 | 0.013 | 0.763 | 1.47 | 1 сутки | 1.47 | 0 | 1.47 | 0.707 | 0.707 | открыт
128 | ПС 35/10 Шуклино | 1 х 2,5 |  | 0.25 | 0.85 | 1 сутки | 0.85 | 0 | 0.85 | 0.6 | 0.6 | открыт
129 | ПС 35/10 Элеватор | 1х6,3 |  | 0.31 | 0.6 | 1 сутки | 0.6 | 0 | 0.6 | 0.29 | 0.29 | открыт
130 | ПС 35/10 Яньково | 1 х 1,6 |  | 0.25 | 0.64 | 1 сутки | 0.64 | 0 | 0.64 | 0.39 | 0.39 | открыт
131 | ПС 35/10 Ясенки | 1 х 2,5 | 0.038 | 0.518 | 2.15 | 1 сутки | 2.15 | 0 | 2.15 | 1.632 | 1.632 | открыт
Двух- и более трансформаторные ПС
1 | ПС 110/6 Аккумуляторная | 2*25 |  | 10.47 | 0 | 0 | 10.47 | 0 | 26.25 | 15.78 | 15.78 | открыт
2 | ПС 110/10 АРЗ | 6,3+10,0 |  | 2.62 | 0.9 | 45 | 1.72 | 0 | 6.62 | 4.9 | 4.9 | открыт
3 | ПС 110/35/10 Атомград | 2*25 | 0.188 | 13.258 | 20.2 | 120 | -6.942 | 0 | 26.25 | 33.192 | 25.959 | открыт
| Ном. Мощность СН, МВА | 25 | 0.127 | 3.367 | 10.6 | 120 | -7.233 | 0 | 26.25 | 33.483
| Ном. Мощность НН, МВА | 25 | 0.061 | 9.891 | 9.6 | 120 | 0.291 | 0 | 26.25 | 25.959
4 | ПС 110/10 Б. Жирово | 2*6,3 |  | 0.36 | 0.6 | 120 | -0.24 | 0 | 6.62 | 6.86 | 6.86 | открыт
5 | ПС 110/35/10 Басово | 5,6+10,0 | 0.012 | 1.202 | 6.19 | 15 | -4.988 | 0 | 5.88 | 10.868 | 5.379 | открыт
| Ном. Мощность СН, МВА | 5,6+10,0 | 0.011 | 0.511 | 6 |  | -5.489 | 0 | 5.88 | 11.369
| Ном. Мощность НН, МВА | 5,6+10,0 | 0.001 | 0.691 | 0.19 | 120 | 0.501 | 0 | 5.88 | 5.379
6 | ПС 110/35/10 Белая | 2*16,0 | 1.002 | 9.402 | 12 | 120 | -2.598 | 0 | 16.8 | 19.398 | 12.678 | открыт
| Ном. Мощность СН, МВА | 16 | 0.722 | 4.122 | 0 |  | 4.122 | 0 | 16.8 | 12.678
| Ном. Мощность НН, МВА | 16 | 0.28 | 5.28 | 12 | 120 | -6.72 | 0 | 16.8 | 23.52
7 | ПС 110/35/10 Бобрышово | 2*6,3 | 0.036 | 1.236 | 1.3 | 120 | -0.064 | 0 | 6.62 | 6.684 | 6.016 | открыт
| Ном. Мощность СН, МВА | 6.3 | 0.004 | 4: 0.604; Мин. 7: 0.604; Мин. 8: 0; Мин. 9: 6.62; Мин. 10: 6.016
| Ном. Мощность НН, МВА | 6.3 | 0.032 | 0.632 | 1.3 | 120 | -0.668 | 0 | 6.62 | 7.288
8 | ПС 110/10 Винниково | 2,5+6,3 | 0.044 | 2.354 | 1.17 | 45 | 1.184 | 0 | 2.63 | 1.446 | 1.446 | открыт
9 | ПС 110/35/6 Волокно | 40,0+2*40,5 | 1.538 | 39.118 | 16.8 | 0 | 22.318 | 0 | 84.53 | 62.212 | 61.196 | открыт
| Ном. Мощность СН, МВА | 40,0+2*40,5 | 1.454 | 15.784 | 16.8 | 0 | -1.016 | 0 | 84.53 | 85.546
| Ном. Мощность НН, МВА | 40,0+2*40,5 | 0.084 | 23.334 | 0 | 0 | 23.334 | 0 | 84.53 | 61.196
10 | ПС 110/10 Высокая | 2*16,0 |  | 28.27 | 3.2 | 15 | 25.07 | 0 | 16.8 | -8.27 | -8.27 | закрыт
11 | ПС 110/35/10 Глушково | 2*10,0 | 0.5613 | 9.2613 | 8.04 | 120 | 1.2213 | 0 | 10.5 | 9.2787 | 8.4347 | открыт
| Ном. Мощность СН, МВА | 10 | 0.556 | 5.756 | 6.6 | 120 | -0.844 | 0 | 10.5 | 11.344
| Ном. Мощность НН, МВА | 10 | 0.0053 | 3.5053 | 1.44 | 80 | 2.0653 | 0 | 10.5 | 8.4347
12 | ПС 110/10 Городская | 2*25,0 | 4.53 | 14.93 | 0 | 0 | 14.93 | 0 | 26.25 | 11.32 | 11.32 | открыт
13 | ПС 110/35/10 Горшечное | 10+16,0 | 0.674 | 10.084 | 6.52 | 120 | 3.564 | 0 | 10.5 | 6.936 | 6.936 | открыт
| Ном. Мощность СН, МВА | 10+16,0 | 0.297 | 6.427 | 6.06 |  | 0.367 | 0 | 10.5 | 10.133
| Ном. Мощность НН, МВА | 10+16,0 | 0.377 | 3.657 | 0.46 | 120 | 3.197 | 0 | 10.5 | 7.303
14 | ПС 110/35/10 Дмитриев | 2*10,0 | 0.231 | 7.321 | 10.4 | 120 | -3.079 | 0 | 10.5 | 13.579 | 8.219 | открыт
| Ном. Мощность СН, МВА | 10 | 0.02 | 2.04 | 7.4 |  | -5.36 | 0 | 10.5 | 15.86
| Ном. Мощность НН, МВА | 10 | 0.211 | 5.281 | 3 | 80 | 2.281 | 0 | 10.5 | 8.219
15 | ПС 110/6 Долгие Буды | 2*10,0 | 0.017 | 0.817 | 0.5 | 120 | 0.317 | 0 | 10.5 | 10.183 | 10.183 | открыт
16 | ПС 110/35/10 Золотухино | 2*25,0 | 0.314 | 7.074 | 23.57 | 80 | -16.496 | 0 | 26.25 | 42.746 | 25.36 | открыт
| Ном. Мощность СН, МВА | 25 | 0.084 | 2.884 | 18.8 |  | -15.916 | 0 | 26.25 | 42.166
| Ном. Мощность НН, МВА | 25 | 0.23 | 4.19 | 3.3 | 120 | 0.89 | 0 | 26.25 | 25.36
17 | ПС 110/35/10 Камыши | 2*6,3 | 3.999 | 12.589 | 5.45 | 20 | 7.139 | 0 | 6.62 | -0.519 | -0.84 | закрыт
| Ном. Мощность СН, МВА | 6.3 | 3.91 | 10.91 | 3.45 |  | 7.46 | 0 | 6.62 | -0.84
| Ном. Мощность НН, МВА | 6.3 | 0.089 | 1.679 | 2 | 20 | -0.321 | 0 | 6.62 | 6.941
18 | ПС 110/35/10 Касторное | 15,0+16,0 | 0.444 | 14.574 | 6.97 | 120 | 7.604 | 0 | 15.75 | 8.146 | 8.146 | открыт
| Ном. Мощность СН, МВА | 15,0+16,0 | 0.358 | 10.988 | 6.6 |  | 4.388 | 0 | 15.75 | 11.362
| Ном. Мощность НН, МВА | 15,0+16,0 | 0.086 | 3.586 | 0.37 | 120 | 3.216 | 0 | 15.75 | 12.534
19 | ПС 110/35/10 Киликино | 2*16,0 | 0.063 | 2.593 | 6.9 | 120 | -4.307 | 0 | 16.8 | 21.107 | 18.51 | открыт
| Ном. Мощность СН, МВА | 16 | 0.063 | 2.403 | 5 |  | -2.597 | 0 | 16.8 | 19.397
| Ном. Мощность НН, МВА | 16 |  | 0.19 | 1.9 | 120 | -1.71 | 0 | 16.8 | 18.51
20 | ПС 110/35/6 Кировская | 2*40,0 | 2.57 | 56.23 | 16.36 | 120 | 39.87 | 0 | 42 | 2.13 | 2.13 | открыт
| Ном. Мощность СН, МВА | 40 |  | 26.67 | 13.06 | 120 | 13.61 | 0 | 42 | 28.39
| Ном. Мощность НН, МВА | 40 | 2.57 | 29.56 | 3.3 | 120 | 26.26 | 0 | 42 | 15.74
21 | ПС 110/35/10 Клюква | 2*16,0 | 0.345 | 3.625 | 1.2 | 120 | 2.425 | 0 | 16.8 | 14.375 | 14.375 | открыт
| Ном. Мощность СН, МВА | 16 |  | 4: 0; Мин. 7: 0; Мин. 8: 0; Мин. 9: 16.8; Мин. 10: 16.8
| Ном. Мощность НН, МВА | 16 | 0.345 | 3.625 | 1.2 | 120 | 2.425 | 0 | 16.8 | 14.375
22 | ПС 110/10 Компрессорная | 2*40,0 |  | 1.11 | 0 | 0 | 1.11 | 0 | 42 | 40.89 | 40.89 | открыт
23 | ПС 110/35/10 Конышевка | 10,0+16,0 | 1.072 | 10.132 | 8 | 120 | 2.132 | 0 | 10.5 | 8.368 | 8.368 | открыт
| Ном. Мощность СН, МВА | 10,0+16,0 | 0.097 | 7.037 | 5.9 |  | 1.137 | 0 | 10.5 | 9.363
| Ном. Мощность НН, МВА | 10,0+16,0 | 0.975 | 3.095 | 2.1 |  | 0.995 | 0 | 10.5 | 9.505
24 | ПС 110/10 Котельная | 10,0+25,0 | 3.62 | 11.42 | 2.1 | 0 | 9.32 | 0 | 10.5 | 1.18 | 1.18 | открыт
25 | ПС 110/35/10 Кшень | 2*10,0 | 1.859 | 10.589 | 6.63 | 10 | 3.959 | 0 | 10.5 | 6.541 | 5.149 | открыт
| Ном. Мощность СН, МВА | 10 | 0.418 | 4.668 | 6.06 |  | -1.392 | 0 | 10.5 | 11.892
| Ном. Мощность НН, МВА | 10 | 1.441 | 5.921 | 0.57 | 120 | 5.351 | 0 | 10.5 | 5.149
26 | ПС 110/6 Лесная | 2*40,0 |  | 2.37 | 0 | 0 | 2.37 | 0 | 42 | 39.63 | 39.63 | открыт
27 | ПС 110/35/10 Льгов | 2*25,0 | 0.345 | 13.485 | 4 | 120 | 9.485 | 0 | 26.25 | 16.765 | 2.675 | открыт
| Ном. Мощность СН, МВА | 25 | 0 | 4: 1.66; Мин. 7: 1.66; Мин. 8: 0; Мин. 9: 10.5; Мин. 10: 8.84
| Ном. Мощность НН, МВА | 25 | 0.345 | 11.825 | 4 | 120 | 7.825 | 0 | 10.5 | 2.675
28 | ПС 110/35/10 Лукашевка | 2*16,0 | 0.057 | 8.327 | 10.6 | 120 | -2.273 | 0 | 16.8 | 19.073 | 16.973 | открыт
| Ном. Мощность СН, МВА | 16 | 0.057 | 5.127 | 5.3 |  | -0.173 | 0 | 16.8 | 16.973
| Ном. Мощность НН, МВА | 16 |  | 3.2 | 5.3 | 120 | -2.1 | 0 | 16.8 | 18.9
29 | ПС 110/35/10 Любостань | 6,3+10,0 | 0.126 | 5.726 | 13.1 | 120 | -7.374 | 0 | 6.62 | 13.994 | 7.315 | открыт
| Ном. Мощность СН, МВА | 6,3+10,0 | 0.121 | 5.121 | 11.8 |  | -6.679 | 0 | 6.62 | 13.299
| Ном. Мощность НН, МВА | 6,3+10,0 | 0.005 | 0.605 | 1.3 |  | -0.695 | 0 | 6.62 | 7.315
30 | ПС 110/35/6 Мантурово | 2*16,0 | 0.419 | 6.999 | 9.35 | 10 | -2.351 | 0 | 16.8 | 19.151 | 16.86 | открыт
| Ном. Мощность СН, МВА | 16 | 0.419 | 6.799 | 9.09 |  | -2.291 | 0 | 16.8 | 19.091
| Ном. Мощность НН, МВА | 16 |  | 0.2 | 0.26 | 120 | -0.06 | 0 | 16.8 | 16.86
31 | ПС 110/35/10 8-е Марта | 6,3+10,0 | 3.919 | 10.989 | 9.6 | 120 | 1.389 | 0 | 6.62 | 5.231 | 3.497 | открыт
| Ном. Мощность СН, МВА | 6,3+10,0 | 3.913 | 9.723 | 6.6 | 120 | 3.123 | 0 | 6.62 | 3.497
| Ном. Мощность НН, МВА | 6,3+10,0 | 0.006 | 1.266 | 3 | 45 | -1.734 | 0 | 6.62 | 8.354
32 | ПС 110/10 Мартовская | 2*6,3 | 0.288 | 1.028 | 0.55 | 120 | 0.478 | 0 | 6.62 | 6.142 | 6.142 | открыт
33 | ПС 110/35/10 Марьино | 10,0+25,0 | 0.102 | 6.252 | 8.11 | 120 | -1.858 | 0 | 10.5 | 12.358 | 11.251 | открыт
| Ном. Мощность СН, МВА | 10,0+25,0 | 0.083 | 3.793 | 4.9 |  | -1.107 | 0 | 10.5 | 11.607
| Ном. Мощность НН, МВА | 10,0+25,0 | 0.019 | 2.459 | 3.21 |  | -0.751 | 0 | 10.5 | 11.251
34 | ПС 110/35/10 Медвенка | 2*10,0 | 0.377 | 6.327 | 19.22 | 120 | -12.893 | 0 | 10.5 | 23.393 | 8.612 | открыт
| Ном. Мощность СН, МВА | 10 | 0.249 | 2.319 | 17.1 |  | -14.781 | 0 | 10.5 | 25.281
| Ном. Мощность НН, МВА | 10 | 0.128 | 4.008 | 2.12 | 120 | 1.888 | 0 | 10.5 | 8.612
35 | ПС 110/6 Нефтяная | 2*10,0 |  | 0.28 |  |  | 0.28 | 0 | 10.5 | 10.22 | 10.22 | открыт
36 | ПС 110/35/10 Обоянь | 16,0 + 25,0 | 0.879 | 16.979 | 26.86 | 120 | -9.881 | 0 | 16.8 | 26.681 | 11.328 | открыт
| Ном. Мощность СН, МВА | 16,0 + 25,0 | 0.047 | 2.047 | 17.4 | 0 | -15.353 | 0 | 16.8 | 32.153
| Ном. Мощность НН, МВА | 16,0 + 25,0 | 0.832 | 14.932 | 9.46 |  | 5.472 | 0 | 16.8 | 11.328
37 | ПС 110/35/10 Октябрьская | 2 х 16,0 | 0.392 | 9.012 | 15.5 | 120 | -6.488 | 0 | 16.8 | 23.288 | 14.437 | открыт
| Ном. Мощность СН, МВА | 16 | 0.109 | 5.649 | 14.5 |  | -8.851 | 0 | 16.8 | 25.651
| Ном. Мощность НН, МВА | 16 | 0.283 | 3.363 | 1 | 120 | 2.363 | 0 | 16.8 | 14.437
38 | ПС 110/35/10 Ольховка | 2 х 6,3 | 0.052 | 1.972 | 6.31 | 120 | -4.338 | 0 | 6.62 | 10.958 | 7.691 | открыт
| Ном. Мощность СН, МВА | 6.3 | 0.033 | 1.733 | 5 | 120 | -3.267 | 0 | 6.62 | 9.887
| Ном. Мощность НН, МВА | 6.3 | 0.019 | 0.239 | 1.31 | 120 | -1.071 | 0 | 6.62 | 7.691
39 | ПС 110/10 Паники | 2 х 2,5 |  | 0.79 | 0.1 | 120 | 0.69 | 0 | 2.63 | 1.94 | 1.94 | открыт
40 | ПС 110/35/10 Пены | 2 х 16,0 | 0.138 | 9.768 | 6.9 | 120 | 2.868 | 0 | 16.8 | 13.932 | 13.932 | открыт
| Ном. Мощность СН, МВА | 16 | 0.118 | 4.488 | 3.5 |  | 0.988 | 0 | 16.8 | 15.812
| Ном. Мощность НН, МВА | 16 | 0.02 | 5.28 | 3.4 | 120 | 1.88 | 0 | 16.8 | 14.92
41 | ПС 110/35/10 Прибор | 2 х 25,0 | 0 | 32.12 | 6.5 | 0 | 25.62 | 0 | 26.25 | 0.63 | 0.63 | открыт
| Ном. Мощность СН, МВА | 25 |  | 4: 0; Мин. 7: 0; Мин. 8: 0; Мин. 9: 26.25; Мин. 10: 26.25
| Ном. Мощность НН, МВА | 25 |  | 32.12 | 6.5 | 0 | 25.62 | 0 | 26.25 | 0.63
42 | ПС 110/10 Прогресс | 2 х 63,0 |  | 23.2 | 0 | 0 | 23.2 | 0 | 66.2 | 43 | 43 | открыт
43 | ПС 110/10 ПТФ | 6,3 + 10,0 |  | 5.92 | 0 | 0 | 5.92 | 0 | 6.62 | 0.7 | 0.7 | открыт
44 | ПС 110/35/10 Р. Буды | 2 х 10,0 | 0.007 | 3.407 | 15.7 | 120 | -12.293 | 0 | 10.5 | 22.793 | 15.493 | открыт
| Ном. Мощность СН, МВА | 10 | 0 | 2 | 9.3 |  | -7.3 | 0 | 10.5 | 17.8
| Ном. Мощность НН, МВА | 10 | 0.007 | 1.407 | 6.4 |  | -4.993 | 0 | 10.5 | 15.493
45 | ПС 110/35/10 Разиньково | 6,3 + 10,0 | 0.418 | 3.318 | 21.4 | 45 | -18.082 | 0 | 6.62 | 24.702 | 9.175 | открыт
| Ном. Мощность СН, МВА | 6,3 + 10,0 | 0.323 | 2.273 | 17.8 |  | -15.527 | 0 | 6.62 | 22.147
| Ном. Мощность НН, МВА | 6,3 + 10,0 | 0.095 | 1.045 | 3.6 | 45 | -2.555 | 0 | 6.62 | 9.175
46 | ПС 110/35/10 Рудная | 2 х 31,5 | 0.542 | 20.632 | 3.25 | 10 | 17.382 | 0 | 33.1 | 15.718 | 15.718 | открыт
| Ном. Мощность СН, МВА | 31.5 | 0.528 | 14.758 | 1.7 |  | 13.058 | 0 | 33.1 | 20.042
| Ном. Мощность НН, МВА | 31.5 | 0.014 | 5.874 | 1.55 | 120 | 4.324 | 0 | 33.1 | 28.776
47 | ПС 110/35/10 Рыльск | 16,0 + 25,0 | 4.086 | 23.036 | 11 | 120 | 12.036 | 0 | 16.8 | 4.764 | 4.764 | открыт
| Ном. Мощность СН, МВА | 16,0 + 25,0 | 4.028 | 16.928 | 7 |  | 9.928 | 0 | 16.8 | 6.872
| Ном. Мощность НН, МВА | 16,0 + 25,0 | 0.058 | 6.108 | 4 | 120 | 2.108 | 0 | 16.8 | 14.692
48 | ПС 110/10 Соловьиная | 2 х 25,0 |  | 6.91 | 0 | 0 | 6.91 | 0 | 26.25 | 19.34 | 19.34 | открыт
49 | ПС 110/10 СТК | 2 х 10,0 |  | 1.91 | 0 | 0 | 1.91 | 0 | 10.5 | 8.59 | 8.59 | открыт
50 | ПС 110/10 Студенок | 2 х 6,3 | 0.098 | 3.718 | 0.7 | 120 | 3.018 | 0 | 6.62 | 3.602 | 3.602 | открыт
51 | ПС 110/35/10 Суджа | 2 х 25,0 | 1.119 | 17.619 | 29 | 120 | -11.381 | 0 | 26.25 | 37.631 | 27.44 | открыт
| Ном. Мощность СН, МВА | 25 | 0.509 | 6.909 | 17.1 |  | -10.191 | 0 | 26.25 | 36.441
| Ном. Мощность НН, МВА | 25 | 0.61 | 10.71 | 11.9 |  | -1.19 | 0 | 26.25 | 27.44
52 | ПС 110/35/10 Счетмаш | 2 х 25,0 | 6.586 | 20.186 | 0 | 0 | 20.186 | 0 | 26.25 | 6.064 | 6.064 | открыт
| Ном. Мощность СН, МВА | 25 | 1.086 | 4: 4.986; Мин. 7: 4.986; Мин. 8: 0; Мин. 9: 26.25; Мин. 10: 21.264
| Ном. Мощность НН, МВА | 25 | 5.5 | 15.2 | 0 | 0 | 15.2 | 0 | 26.25 | 11.05
53 | ПС 110/35/10 Теткино | 2 х 10,0 | 0.052 | 5.562 | 3.44 | 120 | 2.122 | 0 | 10.5 | 8.378 | 7.595 | открыт
| Ном. Мощность СН, МВА | 10 | 0.017 | 1.217 | 2 |  | -0.783 | 0 | 10.5 | 11.283
| Ном. Мощность НН, МВА | 10 | 0.035 | 4.345 | 1.44 |  | 2.905 | 0 | 10.5 | 7.595
54 | ПС 110/35/10 Тим | 6,3 + 16,0 | 0.408 | 6.108 | 9.59 | 120 | -3.482 | 0 | 6.62 | 10.102 | 4.937 | открыт
| Ном. Мощность СН, МВА | 6,3 + 16,0 | 0.325 | 3.925 | 9.09 |  | -5.165 | 0 | 6.62 | 11.785
| Ном. Мощность НН, МВА | 6,3 + 16,0 | 0.083 | 2.183 | 0.5 | 120 | 1.683 | 0 | 6.62 | 4.937
55 | ПС 110/35/10 Уютное | 10,0 + 16,0 | 0.01 | 1.02 | 0.5 | 120 | 0.52 | 0 | 10.5 | 9.98 | 9.83 | открыт
| Ном. Мощность СН, МВА | 10,0 + 16,0 | 0 | 4: 0.67; Мин. 7: 0.67; Мин. 8: 0; Мин. 9: 10.5; Мин. 10: 9.83
| Ном. Мощность НН, МВА | 10,0 + 16,0 | 0.01 | 0.35 | 0.5 | 120 | -0.15 | 0 | 10.5 | 10.65
56 | ПС 110/35/10 Фатеж | 2 х 16,0 | 1.381 | 7.701 | 17.4 | 120 | -9.699 | 0 | 16.8 | 26.499 | 16.951 | открыт
| Ном. Мощность СН, МВА | 16 | 1.252 | 3.252 | 12.8 |  | -9.548 | 0 | 16.8 | 26.348
| Ном. Мощность НН, МВА | 16 | 0.129 | 4.449 | 4.6 | 120 | -0.151 | 0 | 16.8 | 16.951
57 | ПС 110/35/10 Фосфоритная | 2 х 25,0 | 0.142 | 5.582 | 12.34 | 120 | -6.758 | 0 | 26.25 | 33.008 | 24.4 | открыт
| Ном. Мощность СН, МВА | 25 | 0.132 | 3.512 | 12.12 |  | -8.608 | 0 | 26.25 | 34.858
| Ном. Мощность НН, МВА | 25 | 0.01 | 2.07 | 0.22 | 10 | 1.85 | 0 | 26.25 | 24.4
58 | ПС 110/35/10 Хомутовка | 7,5 + 10,0 | 0.134 | 5.824 | 6.3 | 80 | -0.476 | 0 | 7.88 | 8.356 | 5.204 | открыт
| Ном. Мощность СН, МВА | 7,5 + 10,0 | 0.018 | 0.748 | 3.9 |  | -3.152 | 0 | 7.88 | 11.032
| Ном. Мощность НН, МВА | 7,5 + 10,0 | 0.116 | 5.076 | 2.4 | 80 | 2.676 | 0 | 7.88 | 5.204
59 | ПС 110/35/10 Черемисиново | 2 х 16,0 | 0.294 | 6.444 | 9.38 | 10 | -2.936 | 0 | 16.8 | 19.736 | 14.943 | открыт
| Ном. Мощность СН, МВА | 16 | 0.177 | 4.297 | 9.09 |  | -4.793 | 0 | 16.8 | 21.593
| Ном. Мощность НН, МВА | 16 | 0.117 | 2.147 | 0.29 | 120 | 1.857 | 0 | 16.8 | 14.943
60 | ПС 110/35/10 Черемошки | 2 х 6,3 | 0.064 | 3.404 | 8.25 | 120 | -4.846 | 0 | 6.62 | 11.466 | 7.085 | открыт
| Ном. Мощность СН, МВА | 6.3 | 0.059 | 2.619 | 7 |  | -4.381 | 0 | 6.62 | 11.001
| Ном. Мощность НН, МВА | 6.3 | 0.005 | 0.785 | 1.25 | 129 | -0.465 | 0 | 6.62 | 7.085
61 | ПС 110/35/10 Шумаково | 2 х 10,0 | 0.344 | 4.744 | 13.73 | 120 | -8.986 | 0 | 10.5 | 19.486 | 11.938 | открыт
| Ном. Мощность СН, МВА | 10 | 0.252 | 3.652 | 11.2 |  | -7.548 | 0 | 10.5 | 18.048
| Ном. Мощность НН, МВА | 10 | 0.092 | 1.092 | 2.53 | 120 | -1.438 | 0 | 10.5 | 11.938
62 | ПС 110/35/10 Щигры | 2 х 25,0 | 0.564 | 11.844 | 12.9 | 120 | -1.056 | 0 | 26.5 | 27.556 | 21.341 | открыт
| Ном. Мощность СН, МВА | 25 | 0.355 | 5.905 | 12.12 |  | -6.215 | 0 | 26.5 | 32.715
| Ном. Мощность НН, МВА | 25 | 0.209 | 5.939 | 0.78 | 120 | 5.159 | 0 | 26.5 | 21.341
63 | ПС 110/35/10 Ястребовка | 7,5 + 10,0 | 0.2097 | 2.7697 | 6.31 | 10 | -3.5403 | 0 | 7.88 | 11.4203 | 6.9 | открыт
| Ном. Мощность СН, МВА | 7,5 + 10,0 | 0.1597 | 1.5397 | 6.06 |  | -4.5203 | 0 | 7.88 | 12.4003
| Ном. Мощность НН, МВА | 7,5 + 10,0 | 0.05 | 1.23 | 0.25 | 10 | 0.98 | 0 | 7.88 | 6.9
64 | ПС 35/10 Амосовка | 2 х 2,5 | 0.008 | 0.318 | 0.2 | 120 | 0.118 | 0 | 2.63 | 2.512 | 2.512 | открыт
65 | ПС 35/10 Афанасьевка (ЮЭС) | 1,6 + 2,5 |  | 0.5 | 0.37 | 120 | 0.13 | 0 | 1.68 | 1.55 | 1.55 | открыт
66 | ПС 35/10 Б.Солдатское 2 | 2 х 4,0 |  | 1.4 | 1.1 | 80 | 0.3 | 0 | 4.2 | 3.9 | 3.9 | открыт
67 | ПС 35/10 Б.Змеинец | 2 х 1,6 | 0.01 | 0.24 | 1.43 | 120 | -1.19 | 0 | 1.68 | 2.87 | 2.87 | открыт
68 | ПС 35/10 Безлесная | 2 х 4,0 | 0.253 | 1.443 | 6.1 | 0 | -4.657 | 0 | 4.2 | 8.857 | 8.857 | открыт
69 | ПС 35/10 Береза | 1,0 + 2,5 | 0.016 | 0.506 | 0.15 | 120 | 0.356 | 0 | 1.05 | 0.694 | 0.694 | открыт
70 | ПС 35/10 Благодать | 2,5 + 4,0 | 0.076 | 1.066 | 0.29 | 120 | 0.776 | 0 | 2.63 | 1.854 | 1.854 | открыт
71 | ПС 35/10 Быканово | 2 х 2,5 | 0.029 | 0.529 | 0.41 | 120 | 0.119 | 0 | 2.63 | 2.511 | 2.511 | открыт
72 | ПС 35/10 В. Любаж | 4,0 + 10,0 | 0.55 | 1.72 | 0.4 | 120 | 1.32 | 0 | 4.2 | 2.88 | 2.88 | открыт
73 | ПС 35/10 Веселое | 2 х 1,6 | 0.453 | 1.253 | 0.22 | 120 | 1.033 | 0 | 1.68 | 0.647 | 0.647 | открыт
74 | ПС 35/10 Волобуевка | 2,5 + 4,0 | 0.044 | 0.614 | 0.46 | 120 | 0.154 | 0 | 2.63 | 2.476 | 2.476 | открыт
75 | ПС 35/10 Воропаево | 2 х 4,0 | 0.025 | 0.895 | 0 | 0 | 0.895 | 0 | 4.2 | 3.305 | 3.305 | открыт
76 | ПС 35/10 Восточная | 2 х 6,3 | 0.189 | 4.319 | 0.46 | 120 | 3.859 | 0 | 6.62 | 2.761 | 2.761 | открыт
77 | ПС 35/10 Выгорное | 2 х 2,5 | 0.108 | 1.328 | 0.51 | 120 | 0.818 | 0 | 2.63 | 1.812 | 1.812 | открыт
78 | ПС 35/10 Гастомля | 2 х 1,6 | 0.009 | 0.309 | 0.17 | 120 | 0.139 | 0 | 1.68 | 1.541 | 1.541 | открыт
79 | ПС 35/10 Городок | 2 х 4,0 |  | 1.6 | 0.7 | 45 | 0.9 | 0 | 4.2 | 3.3 | 3.3 | открыт
80 | ПС 35/10 Гуево | 2 х 2,5 | 0.04 | 1.24 | 1.69 | 20 | -0.45 | 0 | 2.63 | 3.08 | 3.08 | открыт
81 | ПС 35/10 Долженково | 2 х 1,6 | 0.042 | 0.442 | 0.38 | 120 | 0.062 | 0 | 1.68 | 1.618 | 1.618 | открыт
82 | ПС 35/6 Духовец | 2,5 + 4,0 | 0.115 | 3.445 | 3.5 | 0 | -0.055 | 0 | 2.63 | 2.685 | 2.685 | открыт
83 | ПС 35/10 Жерновец | 2 х 2,5 | 0.005 | 0.405 | 0.26 | 120 | 0.145 | 0 | 2.63 | 2.485 | 2.485 | открыт
84 | ПС 35/6 Западная | 2 х 10,0 | 0.01 | 12.58 | 2.5 | 0 | 10.08 | 0 | 10.5 | 0.42 | 0.42 | открыт
85 | ПС 35/10 Золотухинская КРС | 2 х 4,0 | 0.625 | 1.725 | 1.67 | 0 | 0.055 | 0 | 4.2 | 4.145 | 4.145 | открыт
86 | ПС 35/10 Зуевка | 1,6 + 2,5 | 0.108 | 1.008 | 0.93 | 45 | 0.078 | 0 | 1.68 | 1.602 | 1.602 | открыт
87 | ПС 35/10 Иванино | 2 х 6,3 | 0.036 | 2.226 | 2.69 | 80 | -0.464 | 0 | 6.62 | 7.084 | 7.084 | открыт
88 | ПС 35/10 Калиновка | 1,8 + 2,5 |  | 0.68 | 0.5 | 120 | 0.18 | 0 | 1.89 | 1.71 | 1.71 | открыт
89 | ПС 35/10 Кириловка | 2 х 1,6 | 0.015 | 0.305 | 0.52 | 120 | -0.215 | 0 | 1.68 | 1.895 | 1.895 | открыт
90 | ПС 35/6 Кислинская | 2 х 10,0 | 0.409 | 17.109 | 6.25 | 20 | 10.859 | 0 | 10.5 | -0.359 | -0.359 | закрыт
91 | ПС 35/10 Комбизавод | 4,0+6,3 |  | 0.29 | 0 | 0 | 0.29 | 0 | 4.2 | 3.91 | 3.91 | открыт
92 | ПС 35/10 Комбикормовый завод | 2 х 6,3 | 0.083 | 3.393 | 0.21 | 120 | 3.183 | 0 | 6.62 | 3.437 | 3.437 | открыт
93 | ПС 35/10 Коммунальная | 3,2 + 4,0 |  | 2.66 | 1.14 | 80 | 1.52 | 0 | 3.36 | 1.84 | 1.84 | открыт
94 | ПС 35/10 Коренево | 4,0 + 6,3 | 3.77 | 7.22 | 2.7 | 80 | 4.52 | 0 | 4.2 | -0.32 | -0.32 | закрыт
95 | ПС 35/10 Кремяное | 2,5 + 4,0 |  | 0.41 | 0.24 | 120 | 0.17 | 0 | 2.63 | 2.46 | 2.46 | открыт
96 | ПС 35/10 Крупец | 1,8 + 2,5 | 0.164 | 1.764 | 0.42 | 120 | 1.344 | 0 | 1.89 | 0.546 | 0.546 | открыт
97 | ПС 35/10 Кульбаки | 2 х 2,5 | 0.009 | 0.889 | 0.6 | 120 | 0.289 | 0 | 2.63 | 2.341 | 2.341 | открыт
98 | ПС 35/10 Культпросвет | 2 х 2,5 | 0.003 | 0.183 | 0.17 | 120 | 0.013 | 0 | 2.63 | 2.617 | 2.617 | открыт
99 | ПС 35/10 Курчатов | 2 х 10,0 | 0.005 | 4.855 | 4.5 | 80 | 0.355 | 0 | 10.5 | 10.145 | 10.145 | открыт
100 | ПС 35/10 Куток | 2 х 2,5 | 0.005 | 0.175 | 0.05 | 120 | 0.125 | 0 | 2.63 | 2.505 | 2.505 | открыт
101 | ПС 35/10 Линец | 2 х 2,5 | 0.016 | 0.686 | 0.25 | 120 | 0.436 | 0 | 2.63 | 2.194 | 2.194 | открыт
102 | ПС 35/10 Луч | 2 х 6,3 | 0.308 | 3.138 | 0.23 | 120 | 2.908 | 0 | 6.62 | 3.712 | 3.712 | открыт
103 | ПС 35/10 Любимовка-2 | 2 х 4,0 | 0.029 | 0.779 | 1.59 | 80 | -0.811 | 0 | 4.2 | 5.011 | 5.011 | открыт
104 | ПС 35/10 Матвеевка | 2 х 2,5 | 0.02 | 0.69 | 0.08 | 120 | 0.61 | 0 | 2.63 | 2.02 | 2.02 | открыт
105 | ПС 35/10 Маяк | 2 х 2,5 | 0.011 | 0.421 | 0.3 | 120 | 0.121 | 0 | 2.63 | 2.509 | 2.509 | открыт
106 | ПС 35/10 Михайловка | 4,0 + 6,3 | 0.14 | 2.29 | 1.7 | 80 | 0.59 | 0 | 4.2 | 3.61 | 3.61 | открыт
107 | ПС 35/10 Мурыновка | 2 х 4,0 | 0.195 | 0.825 | 0.3 | 120 | 0.525 | 0 | 4.2 | 3.675 | 3.675 | открыт
108 | ПС 35/10 Н. Борки | 2 х 2,5 | 0.011 | 0.511 | 0.63 | 120 | -0.119 | 0 | 2.63 | 2.749 | 2.749 | открыт
109 | ПС 35/10 Никольская | 1,6 + 1,8 |  | 0.36 | 0.03 | 80 | 0.33 | 0 | 1.68 | 1.35 | 1.35 | открыт
110 | ПС 35/10 Новая | 2 х 2,5 | 0.246 | 1.326 | 0.4 | 120 | 0.926 | 0 | 2.63 | 1.704 | 1.704 | открыт
111 | ПС 35/10 Орехово | 2 х 2,5 | 0.041 | 0.771 | 0.19 | 120 | 0.581 | 0 | 2.63 | 2.049 | 2.049 | открыт
112 | ПС 35/10 Орловка | 2 х 2,5 | 0.015 | 0.185 | 0.52 | 120 | -0.335 | 0 | 2.63 | 2.965 | 2.965 | открыт
113 | ПС 35/10 Осоцкое | 2 х 2,5 |  | 0.19 | 0.2 | 120 | -0.01 | 0 | 2.63 | 2.64 | 2.64 | открыт
114 | ПС 35/10 Охочевка | 4,0 + 6,3 | 0.172 | 1.442 | 0.74 | 120 | 0.702 | 0 | 4.2 | 3.498 | 3.498 | открыт
115 | ПС 35/10 Панино | 2 х 2,5 | 0.005 | 0.265 | 0.11 | 80 | 0.155 | 0 | 2.63 | 2.475 | 2.475 | открыт
116 | ПС 35/10 Первоавгустовка | 2,5 + 3,2 | 0.037 | 0.777 | 0.52 | 120 | 0.257 | 0 | 2.63 | 2.373 | 2.373 | открыт
117 | ПС 35/10 Петринка | 2,5 + 4,0 | 0.711 | 1.811 | 0.3 | 120 | 1.511 | 0 | 2.63 | 1.119 | 1.119 | открыт
118 | ПС 35/10 Платава | 2 х 2,5 | 0.014 | 1.084 | 0.26 | 120 | 0.824 | 0 | 2.63 | 1.806 | 1.806 | открыт
119 | ПС 35/10 Погожее | 2 х 1,6 | 0.047 | 0.277 | 0.46 | 120 | -0.183 | 0 | 1.68 | 1.863 | 1.863 | открыт
120 | ПС 35/10 Поречное | 2 х 4,0 | 0.008 | 0.508 | 1.16 | 120 | -0.652 | 0 | 4.2 | 4.852 | 4.852 | открыт
121 | ПС 35/10 Почепное | 2 х 6,3 |  | 0.13 | 0.08 | 120 | 0.05 | 0 | 6.62 | 6.57 | 6.57 | открыт
122 | ПС 35/10 Пригородная | 2 х 2,5 | 0.274 | 0.794 | 0.3 | 80 | 0.494 | 0 | 2.63 | 2.136 | 2.136 | открыт
123 | ПС 35/10 Пселец | 2 х 1,6 |  | 0.2 | 0.24 | 120 | -0.04 | 0 | 1.68 | 1.72 | 1.72 | открыт
124 | ПС 35/10 Пузачи | 1,6 + 4,0 | 0.04 | 0.44 | 0.43 | 120 | 0.01 | 0 | 1.68 | 1.67 | 1.67 | открыт
125 | ПС 35/10 Пушкарное | 2 х 2,5 | 0.029 | 0.829 | 0.32 | 120 | 0.509 | 0 | 2.625 | 2.116 | 2.116 | открыт
126 | ПС 35/10 Р.Колодец | 2 х 2,5 | 0.337 | 0.937 | 0.44 | 120 | 0.497 | 0 | 2.625 | 2.128 | 2.128 | открыт
127 | ПС 35/10 Разветье | 2 х 4,0 | 0.388 | 2.768 | 1.03 | 120 | 1.738 | 0 | 4.2 | 2.462 | 2.462 | открыт
128 | ПС 35/10 В. Реутец | 2 х 4,0 | 0.005 | 0.285 | 0.11 | 120 | 0.175 | 0 | 4.2 | 4.025 | 4.025 | открыт
129 | ПС 35/10 Рождественка | 2 х 1,6 | 0.061 | 0.361 | 0.29 | 120 | 0.071 | 0 | 1.68 | 1.609 | 1.609 | открыт
130 | ПС 35/10 Рубильник | 2 х 2,5 | 0.045 | 0.825 | 1.18 | 80 | -0.355 | 0 | 2.625 | 2.98 | 2.98 | открыт
131 | ПС 35/10 Рыжково | 2 х 1,6 | 0.007 | 0.237 | 0.08 | 20 | 0.157 | 0 | 1.68 | 1.523 | 1.523 | открыт
132 | ПС 35/10 Сапогово | 2 х 2,5 | 0.109 | 1.679 | 0.6 | 20 | 1.079 | 0 | 2.63 | 1.551 | 1.551 | открыт
133 | ПС 35/10 Свобода-сельская | 2 х 6,3 | 0.138 | 4.148 | 2.25 | 80 | 1.898 | 0 | 6.615 | 4.717 | 4.717 | открыт
134 | ПС 35/10 Селекционная | 2 х 4,0 | 0.031 | 1.591 | 1.4 | 45 | 0.191 | 0 | 4.2 | 4.009 | 4.009 | открыт
135 | ПС 35/10 Семеновка | 2 х 2,5 | 0.052 | 0.552 | 0 | - | 0.552 | 0 | 2.625 | 2.073 | 2.073 | открыт
136 | ПС 35/10 Семзавод | 2 х 2,5 | 0.049 | 0.649 | 0.6 | 120 | 0.049 | 0 | 2.63 | 2.581 | 2.581 | открыт
137 | ПС 35/10 Снагость | 2 х 4,0 | 0.037 | 1.297 | 0.05 | 10 | 1.247 | 0 | 4.2 | 2.953 | 2.953 | открыт
138 | ПС 35/10 СОМ | 1,6 + 4,0 | 0.062 | 1.622 | 0.08 | 10 | 1.542 | 0 | 1.68 | 0.138 | 0.138 | открыт
139 | ПС 35/10 Сосновый Бор | 3,2 + 4,0 | 0.049 | 0.739 | 0.69 | 120 | 0.049 | 0 | 3.36 | 3.311 | 3.311 | открыт
140 | ПС 35/10 Стаканово | 2 х 2,5 | 0.039 | 1.269 | 0.58 | 80 | 0.689 | 0 | 2.625 | 1.936 | 1.936 | открыт
141 | ПС 35/10 Старково | 2 х 1,6 | 0.009 | 0.439 | 0.2 | 80 | 0.239 | 0 | 1.68 | 1.441 | 1.441 | открыт
142 | ПС 35/10 Старшее | 2 х 1,6 | 0.005 | 0.315 | 0.2 | 120 | 0.115 | 0 | 1.68 | 1.565 | 1.565 | открыт
143 | ПС 35/10 Теплицы | 2 х 4,0 | 0.052 | 2.302 | 1.08 | 45 | 1.222 | 0 | 4.2 | 2.978 | 2.978 | открыт
144 | ПС 35/10 Туровка | 2 х 2,5 | 0.055 | 0.855 | 0.6 | 120 | 0.255 | 0 | 2.63 | 2.375 | 2.375 | открыт
145 | ПС 35/10 Успенка | 2 х 2,5 | 0.021 | 1.211 | 1 | 80 | 0.211 | 0 | 2.63 | 2.419 | 2.419 | открыт
146 | ПС 35/6 Центральная | 2 х 25,0 | 0.005 | 24.905 | 5 | 10 | 19.905 | 0 | 26.25 | 6.345 | 6.345 | открыт
147 | ПС 35/10 Чермошное | 2 х 2,5 |  | 0.4 | 0.5 | 120 | -0.1 | 0 | 4.2 | 4.3 | 4.3 | открыт
148 | ПС 35/10 Шаталовка | 2,5 + 4,0 | 0.031 | 0.341 | 0.21 | 80 | 0.131 | 0 | 2.625 | 2.494 | 2.494 | открыт
149 | ПС 35/10 Шипы | 2 х 2,5 | 0.012 | 0.212 | 0.3 | 120 | -0.088 | 0 | 2.625 | 2.713 | 2.713 | открыт
150 | ПС 35/10 Элеватор | 4,0 + 6,3 | 0.015 | 2.225 | 0.6 | 120 | 1.625 | 0 | 4.2 | 2.575 | 2.575 | открыт
151 | ПС 35/10 Юго-Западная | 1 х 10,0 |  | 9.28 | 4.7 | 80 | 4.58 | 0 | 10.5 | 5.92 | 5.92 | открыт
152 | ПС 35/10 ЖБИ | 2 х 2,5 |  | 1.97 | 3.9 | 120 | -1.93 | 0 | 2.625 | 4.555 | 4.555 | открыт
| ИТОГО: | 3185.9 | 72.9377 | 4: 855.1277; МВА 5: 785.45; Мин. 11: 1144.651
| дефицит |  |  | Мин. 11: -15.349
| профицит |  |  | Мин. 11: 1129.302
Зам.директора по техническим вопросам -
|  | Главный инженер |  | Мин. 9: А.Н. Рудневский

## Курск
No. | Object of main substation, voltage class | Current deficit | [8 empty] | note
|  | Installed power capacity of transformers Sуst. Including their number, pcs/ MVA | Summary total capacity of central substation following the results of measurements of load maximal Sмах , MVA | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit /proficit of main substation, MVA
|  |  |  | MVA | Min.
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
One-transformer substations
1 | SS 110/35/10 Artyukhovka | 1*6,3 | 1.64 | 6.3 | 24 hours | 6.3 | 0 | 6.3 | 4.66 | 1.2 | opened
| Nom. capacity MV, MVA | 6.3 | 1.1 | 2.3 | 24 hours | 2.3 | 0 | 2.3 | 1.2
| Nom. capacity MV, MVA | 6.3 | 0.54 | 4 | 24 hours | 4 | 0 | 4 | 3.46
2 | SS 110/10 Beketovo | 1*6,3 | 0.39 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.76 | 1.76 | opened
3 | SS 110/35/10 Besedino | 1*6,3 | 2.84 | 6.7 | 24 hours | 6.7 | 0 | 6.7 | 3.86 | 0.16 | opened
| Nom. capacity MV, MVA | 6.3 | 0.5 | 4.2 | 24 hours | 4.2 | 0 | 4.2 | 3.7
| Nom. capacity LV, MVA | 6.3 | 2.34 | 2.5 | 24 hours | 2.5 | 0 | 2.5 | 0.16
4 | SS 110/10 Voskhod | 1*10 | 0.8 | 2.5 | 24 hours | 2.5 | 0 | 2.5 | 1.7 | 1.7 | opened
5 | SS 110/35/10 Zhuryatino | 1*6,3 | 0.82 | 6 | 24 hours | 6 | 0 | 6 | 5.18 | 1.48 | opened
| Nom. capacity MV, MVA | 6.3 | 0 | 3.7 | 24 hours | 3.7 | 0 | 3.7 | 3.7
| Nom. capacity LV, MVA | 6.3 | 0.82 | 2.3 | 24 hours | 2.3 | 0 | 2.3 | 1.48
6 | SS 110/35/10 Zhukovka | 1*10 | 1.1 | 5.16 | 120 | 5.16 | 0 | 5.16 | 4.06 | 0.49 | opened
| Nom. capacity MV, MVA | 10 | 0.93 | 4.5 | 24 hours | 4.5 | 0 | 4.5 | 3.57
| Nom. capacity LV, MVA | 10 | 0.17 | 0.66 | 120 | 0.66 | 0 | 0.66 | 0.49
7 | SS 110/10 Zabelye | 1*2,5 | 0.31 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.84 | 1.84 | opened
8 | SS 110/10 Ivnitsa | 1*6,3 | 0.4 | 0.45 | 24 hours | 0.45 | 0 | 0.45 | 0.05 | 0.05 | opened
9 | SS 110/35/10 Lachinovo | 1*10 | 1.28 | 5.13 | 24 hours | 5.13 | 0 | 5.13 | 3.85 | 1 | opened
| Nom. capacity MV, MVA | 10 | 0.75 | 3.6 | 24 hours | 3.6 | 0 | 3.6 | 2.85
| Nom. capacity LV, MVA | 10 | 0.53 | 1.53 | 24 hours | 1.53 | 0 | 1.53 | 1
10 | SS 110/10 Malaya Loknya | 1*10 | 1.2 | 1.21 | 24 hours | 1.21 | 0 | 1.21 | 0.01 | 0.01 | opened
11 | SS 110/35/10 Maritsa | 1*2,5 | 0.99 | 1.92 | 24 hours | 1.92 | 0 | 1.92 | 0.93 | 0.93 | opened
12 | SS 110/35/10 Raskhovets | 1*6,3 | 0.56 | 5.89 | 24 hours | 5.89 | 0 | 5.89 | 5.33 | 1.97 | opened
| Nom. capacity MV, MVA | 6.3 | 0.38 | 3.74 | 24 hours | 3.74 | 0 | 3.74 | 3.36
| Nom. capacity LV, MVA | 6.3 | 0.18 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.97
13 | SS 110/10 Semyonovskaya | 1*2,5 | 0.4 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 1 | 1 | opened
14 | SS 110/6 Teplichnaya | 1*16 | 4.1 | 6.64 | 24 hours | 6.64 | 0 | 6.64 | 2.54 | 2.54 | opened
15 | SS 110/35/10 Troitskaya | 1*10 | 3.01 | 7.5 | 24 hours | 7.5 | 0 | 7.5 | 4.49 | 0.79 | opened
| Nom. capacity MV, MVA | 10 | 2.7 | 6.4 | 24 hours | 6.4 | 0 | 6.4 | 3.7
| Nom. capacity LV, MVA | 10 | 0.31 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.79
16 | SS 35/10 Avtodor | 1*2,5 | 0.46 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0.34 | 0.34 | opened
17 | SS 35/10 Agronom | 1*1,8 | 0.7 | 0.96 | 24 hours | 0.96 | 0 | 0.96 | 0.26 | 0.26 | opened
18 | SS 35/10 Akimovka | 1*2,5 | 0.25 | 0.68 | 24 hours | 0.68 | 0 | 0.68 | 0.43 | 0.43 | opened
19 | SS 35/10 Alekseevka | 1*2,5 | 0.28 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.15 | 1.15 | opened
20 | SS 35/10 Afanasyevka (WPS) | 1*4 | 0.55 | 1.34 | 24 hours | 1.34 | 0 | 1.34 | 0.79 | 0.79 | opened
21 | SS 35/10 B. Gneushevo | 1*2,5 | 0.77 | 0.96 | 24 hours | 0.96 | 0 | 0.96 | 0.19 | 0.19 | opened
22 | SS 35/10 B.Soldatskoe1 | 1*3,2 | 0.78 | 2.83 | 24 hours | 2.83 | 0 | 2.83 | 2.05 | 2.05 | opened
23 | SS 35/10 Banishchi | 1*1,6 | 0.22 | 0.64 | 24 hours | 0.64 | 0 | 0.64 | 0.42 | 0.42 | opened
24 | SS 35/10 Baranovo | 1*4 | 0.46 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 0.97 | 0.97 | opened
25 | SS 35/10 Belgorodka | 1*2,5 | 0.27 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.88 | 1.88 | opened
26 | SS 35/10 Belitsa | 1*4 | 0.6 | 1.76 | 24 hours | 1.76 | 0 | 1.76 | 1.16 | 1.16 | opened
27 | SS 35/10 Biryukovka | 1*1,6 | 0.6 | 0.67 | 24 hours | 0.67 | 0 | 0.67 | 0.07 | 0.07 | opened
28 | SS 35/10 Bobrovka | 1*1,6 | 0.24 | 0.67 | 24 hours | 0.67 | 0 | 0.67 | 0.43 | 0.43 | opened
29 | SS 35/10 Bobrovo | 1*2,5 | 0.42 | 0.76 | 24 hours | 0.76 | 0 | 0.76 | 0.34 | 0.34 | opened
30 | SS 35/10 Budki | 1*1 | 0.09 | 0.64 | 24 hours | 0.64 | 0 | 0.64 | 0.55 | 0.55 | opened
31 | SS 35/10 Bukreevka (CPS) | 1*1,8 | 0.59 | 1.6 | 50 | 1.6 | 0 | 1.6 | 1.01 | 1.01 | opened
32 | SS 35/10 Bukreevka (WPS) | 1*1,6 | 0.21 | 0.64 | 24 hours | 0.64 | 0 | 0.64 | 0.43 | 0.43 | opened
33 | SS 35/10 Burtsevka | 1*1,6 | 0.18 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.25 | 1.25 | opened
34 | SS 35/10 Bykovo | 1*4 | 0.89 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 0.54 | 0.54 | opened
35 | SS 35/10 V. Shchigor | 1*2,5 | 0.12 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 2.03 | 2.03 | opened
36 | SS 35/10 Vanino | 1*2,5 | 0.36 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0.44 | 0.44 | opened
37 | SS 35/10 Vasilyevka | 1*2,5 | 0.64 | 1.05 | 24 hours | 1.05 | 0 | 1.05 | 0.41 | 0.41 | opened
38 | SS 35/10 Water storage | 1*4 | 1.58 | 2.72 | 24 hours | 2.72 | 0 | 2.72 | 1.14 | 1.14 | opened
39 | SS 35/10 Volokonsk | 1*2,5 | 0.3 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.8 | 0.8 | opened
40 | SS 35/10 Vorobyovka | 1*2,5 | 0.65 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.25 | 0.25 | opened
41 | SS 35/10 Voronok | 1*4 | 0.86 | 2.1 | 24 hours | 2.1 | 0 | 2.1 | 1.24 | 1.24 | opened
42 | SS 35/10 Vyazovoe | 1*2,5 | 0.66 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.49 | 1.49 | opened
43 | SS 35/10 Gakhovo | 1*2,5 | 0.21 | 1.8 | 24 hours | 1.8 | 0 | 1.8 | 1.59 | 1.59 | opened
44 | SS 35/10 Generalshino | 1*2,5 | 0.25 | 1.5 | 24 hours | 1.5 | 0 | 1.5 | 1.25 | 1.25 | opened
45 | SS 35/10 Glazovo | 1*2,5 | 0.94 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 0.46 | 0.46 | opened
46 | SS 35/10 Glebovo | 1*2,5 | 0.49 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 0.91 | 0.91 | opened
47 | SS 35/10 Gordeevka | 1*1,6 | 0.12 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.58 | 0.58 | opened
48 | SS 35/10 Gorodensk | 1*1,6 | 0.59 | 0.76 | 24 hours | 0.76 | 0 | 0.76 | 0.17 | 0.17 | opened
49 | SS 35/10 Goryainovo | 1*2,5 | 0.5 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.6 | 0.6 | opened
50 | SS 35/10 12th State stud farm | 1*2,5 | 0.53 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 0.9 | 0.9 | opened
51 | SS 35/10 Grayvoronka | 1*2,5 | 0.5 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 0.93 | 0.93 | opened
52 | SS 35/10 Grinyovka | 1*2,5 | 0.28 | 2.85 | 24 hours | 2.85 | 0 | 2.85 | 2.57 | 2.57 | opened
53 | SS 35/10 Gustomoy | 1*1,6 | 0.21 | 0.94 | 24 hours | 0.94 | 0 | 0.94 | 0.73 | 0.73 | opened
54 | SS 35/10 Daryino | 1*2,5 | 0.4 | 1.8 | 24 hours | 1.8 | 0 | 1.8 | 1.4 | 1.4 | opened
55 | SS 35/10 Demyakino | 1*2,5 | 0.43 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0.37 | 0.37 | opened
56 | SS 35/10 Efrosimovka | 1*1,8 | 0.38 | 1.07 | 24 hours | 1.07 | 0 | 1.07 | 0.69 | 0.69 | opened
57 | SS 35/10 Zhdanovo | 1*2,5 | 0.38 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.47 | 0.47 | opened
58 | SS 35/10 Zashchitnoe | 1*1,6 | 0.32 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.83 | 1.83 | opened
59 | SS 35/10 Zvannoe | 1*2,5 | 0.6 | 0.84 | 24 hours | 0.84 | 0 | 0.84 | 0.24 | 0.24 | opened
60 | SS 35/10 Znamenka | 1*1,8 | 1.01 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.14 | 1.14 | opened
61 | SS 35/10 Iskra | 1*2,5 | 0.16 | 0.58 | 24 hours | 0.58 | 0 | 0.58 | 0.42 | 0.42 | opened
62 | SS 35/10 Kazanka | 1*4 | 0.33 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0.47 | 0.47 | opened
63 | SS 35/10 Kalinovka (new) | 1*2,5 | 0.17 | 1.8 | 24 hours | 1.8 | 0 | 1.8 | 1.63 | 1.63 | opened
64 | SS 35/10 Karyzh | 1*1,6 | 0.18 | 0.64 | 24 hours | 0.64 | 0 | 0.64 | 0.46 | 0.46 | opened
65 | SS 35/10 Kitaevka | 1*1,6 | 0.26 | 0.74 | 24 hours | 0.74 | 0 | 0.74 | 0.48 | 0.48 | opened
66 | SS 35/10 Kobylki | 1*2,5 | 0.68 | 1.53 | 24 hours | 1.53 | 0 | 1.53 | 0.85 | 0.85 | opened
67 | SS 35/10 Kolontaevka | 1*2,5 | 0.26 | 0.84 | 24 hours | 0.84 | 0 | 0.84 | 0.58 | 0.58 | opened
68 | SS 35/10 Kondratovka | 1*1,8 | 0.55 | 1.42 | 24 hours | 1.42 | 0 | 1.42 | 0.87 | 0.87 | opened
69 | SS 35/10 Korovyakovka | 1*1,6 | 0.21 | 0.76 | 24 hours | 0.76 | 0 | 0.76 | 0.55 | 0.55 | opened
70 | SS 35/10 Lezhenki | 1*2,5 | 0.09 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.34 | 1.34 | opened
71 | SS 35/10 Leninskaya | 1*1,8 | 0.67 | 0.73 | 24 hours | 0.73 | 0 | 0.73 | 0.06 | 0.06 | opened
72 | SS 35/10 Lobazovka | 1*2,5 | 0.86 | 1.09 | 24 hours | 1.09 | 0 | 1.09 | 0.23 | 0.23 | opened
73 | SS 35/10 Lugovka | 1*1,6 | 0.54 | 1.29 | 24 hours | 1.29 | 0 | 1.29 | 0.75 | 0.75 | opened
74 | SS 35/10 Lyubava | 1*6,3 | 0.31 | 1.15 | 24 hours | 1.15 | 0 | 1.15 | 0.84 | 0.84 | opened
75 | SS 35/10 Lyubimovka-1 | 1*3,2 | 0 | 0.96 | 24 hours | 0.96 | 0 | 0.96 | 0.96 | 0.96 | opened
76 | SS 35/10 M. Kamenets | 1*1,6 | 0.6 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.5 | 0.5 | opened
77 | SS 35/10 М. Gneushevo | 1*4 | 0.7 | 1.28 | 24 hours | 1.28 | 0 | 1.28 | 0.58 | 0.58 | opened
78 | SS 35/10 М. Kryuki | 1*2,5 | 0.4 | 1.19 | 24 hours | 1.19 | 0 | 1.19 | 0.79 | 0.79 | opened
79 | SS 35/10 Markovo | 1*2,5 | 0.65 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0.15 | 0.15 | opened
80 | SS 35/10 Marmyzhi | 1*2,5 | 0.21 | 1.33 | 24 hours | 1.33 | 0 | 1.33 | 1.12 | 1.12 | opened
81 | SS 35/10 Melovoe | 1*4 | 0.99 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.16 | 1.16 | opened
82 | SS 35/10 Mokva | 1*4 | 0.5 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.65 | 1.65 | opened
83 | SS 35/10 Mokrusheno | 1*1,6 | 0.6 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.5 | 0.5 | opened
84 | SS 35/10 Molotychi | 1*2,5 | 0.4 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.5 | 0.5 | opened
85 | SS 35/10 Mochaki | 1*2,5 | 0.03 | 1.07 | 24 hours | 1.07 | 0 | 1.07 | 1.04 | 1.04 | opened
86 | SS 35/10 N. Vladimirovka | 1*2,5 | 0.08 | 4.3 | 24 hours | 4.3 | 0 | 4.3 | 4.22 | 4.22 | opened
87 | SS 35/10 N. Gurovo | 1*4,0 | 0.73 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.42 | 1.42 | opened
88 | SS 35/10 Nadeyka | 1*2,5 | 0.16 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 1.24 | 1.24 | opened
89 | SS 35/10 Niva | 1*2,5 | 0.4 | 1.56 | 24 hours | 1.56 | 0 | 1.56 | 1.16 | 1.16 | opened
90 | SS 35/10 Olgovka | 1*2,5 | 0.41 | 0.97 | 24 hours | 0.97 | 0 | 0.97 | 0.56 | 0.56 | opened
91 | SS 35/10 Olkhovatka | 1*4 | 0.38 | 0.64 | 24 hours | 0.64 | 0 | 0.64 | 0.26 | 0.26 | opened
92 | SS 35/10 Orositelnaya | 1*4 | 0.93 | 2.97 | 24 hours | 2.97 | 0 | 2.97 | 2.04 | 2.04 | opened
93 | SS 35/10 Peny-2 | 1*2,5 | 0.6 | 2.32 | 24 hours | 2.32 | 0 | 2.32 | 1.72 | 1.72 | opened
94 | SS 35/10 Perestuplino (old) | 1*2,5 | 0.16 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 1.24 | 1.24 | opened
95 | SS 35/10 Perestuplino (new) | 1*2,5 | 0.36 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 1.04 | 1.04 | opened
96 | SS 35/10 Petrovo | 1*6,3 | 1 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.15 | 1.15 | opened
97 | SS 35/10 Petrovskaya | 1*2,5 | 0.03 | 0.74 | 24 hours | 0.74 | 0 | 0.74 | 0.71 | 0.71 | opened
98 | SS 35/10 Pokrovskoe | 1*2,5 | 0.27 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.88 | 1.88 | opened
99 | SS 35/10 Prilepy | 1*1,6 | 0.53 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.62 | 1.62 | opened
100 | SS 35/10 Pristen | 1*4 | 2.3 | 3.3 | 24 hours | 3.3 | 0 | 3.3 | 1 | 1 | opened
101 | SS 35/10 R. Budy 35/10 | 1*4 | 0 | 0.74 | 24 hours | 0.74 | 0 | 0.74 | 0.74 | 0.74 | opened
102 | SS 35/10 Reut | 1*2,5 | 0.16 | 0.86 | 0 | 0.86 | 0 | 0.86 | 0.7 | 0.7 | opened
103 | SS 35/10 Rovenka | 1*1,6 | 0.16 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.27 | 1.27 | opened
104 | SS 35/10 Rodina (NPC) | 1*2,5 | 0.17 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.53 | 0.53 | opened
105 | SS 35/10 Rodina (EPS) | 1*4 | 0.5 | 2.3 | 24 hours | 2.3 | 0 | 2.3 | 1.8 | 1.8 | opened
106 | SS 35/10 Rubanshchina | 1*2,5 | 0.4 | 1.31 | 24 hours | 1.31 | 0 | 1.31 | 0.91 | 0.91 | opened
107 | SS 35/10 Rusanovo | 1*1,8 | 0.39 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.04 | 1.04 | opened
108 | SS 35/10 Ryshkovo | 1*2,5 | 0.56 | 0.94 | 24 hours | 0.94 | 0 | 0.94 | 0.38 | 0.38 | opened
109 | SS 35/10 Ryazanovo | 1*1,6 | 0.58 | 1.15 | 24 hours | 1.15 | 0 | 1.15 | 0.57 | 0.57 | opened
110 | SS 35/10 Sazanovka | 1*2,5 | 0.3 | 1.25 | 24 hours | 1.25 | 0 | 1.25 | 0.95 | 0.95 | opened
111 | SS 35/10 Sergievka | 1*2,5 | 0.4 | 2.7 | 24 hours | 2.7 | 0 | 2.7 | 2.3 | 2.3 | opened
112 | SS 35/10 Sokolye | 1*2,5 | 0.3 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.13 | 1.13 | opened
113 | SS 35/10 Solntsevo | 1*2,5 | 0.9 | 1.76 | 24 hours | 1.76 | 0 | 1.76 | 0.86 | 0.86 | opened
114 | SS 35/10 Spasskoe | 1*1,6 | 0.22 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.88 | 0.88 | opened
115 | SS 35/10 Sr. Olshanka | 1*2,5 | 0.3 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 1.1 | 1.1 | opened
116 | SS 35/10 Streletskaya | 1*2,5 | 0.35 | 1.3 | 24 hours | 1.3 | 0 | 1.3 | 0.95 | 0.95 | opened
117 | SS 35/10 Subbotino | 1*2,5 | 0.6 | 1.34 | 24 hours | 1.34 | 0 | 1.34 | 0.74 | 0.74 | opened
118 | SS 35/10 Sukhaya | 1*1,6 | 0.44 | 0.71 | 24 hours | 0.71 | 0 | 0.71 | 0.27 | 0.27 | opened
119 | SS 35/10 Telmana | 1*2,5 | 0.3 | 1.15 | 24 hours | 1.15 | 0 | 1.15 | 0.85 | 0.85 | opened
120 | SS 35/10 Terebuzh | 1*2,5 | 0.46 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 0.97 | 0.97 | opened
121 | SS 35/10 Fateevka | 1*2,5 | 0.08 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.62 | 0.62 | opened
122 | SS 35/10 Fentisovo | 1*1,6 | 0.17 | 1.72 | 24 hours | 1.72 | 0 | 1.72 | 1.55 | 1.55 | opened
123 | SS 35/10 Chapaevskaya | 1*2,5 | 0.2 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.9 | 0.9 | opened
124 | SS 35/10 Chemerki | 1*1,6 | 0.06 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.79 | 0.79 | opened
125 | SS 35/10 Chizhovka | 1*1,6 | 0.35 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.08 | 1.08 | opened
126 | SS 35/10 Shatilovka | 1*2,5 | 0.16 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.27 | 1.27 | opened
127 | SS 35/10 Sheptukhovka | 1*2,5 | 0.75 | 1.47 | 24 hours | 1.47 | 0 | 1.47 | 0.72 | 0.72 | opened
128 | SS 35/10 Shuklino | 1*2,5 | 0.25 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.6 | 0.6 | opened
129 | SS 35/10 Elevator | 1*6,3 | 0.31 | 0.6 | 24 hours | 0.6 | 0 | 0.6 | 0.29 | 0.29 | opened
130 | SS 35/10 Yankovo | 1*1,6 | 0.25 | 0.64 | 24 hours | 0.64 | 0 | 0.64 | 0.39 | 0.39 | opened
131 | SS 35/10 Yasenki | 1*2,5 | 0.48 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.67 | 1.67 | opened
Two- and more transformer substations
1 | SS 110/6 Akkumulyatornaya | 2*25 | 10.47 | 0 | 0 | 10.47 | 0 | 26.25 | 15.78 | 15.78 | opened
2 | SS 110/10 ARZ | 6,3+10 | 2.62 | 0.9 | 45 | 1.72 | 0 | 6.62 | 4.9 | 4.9 | opened
3 | SS 110/35/10 Atomgrad | 2*25 | 13.07 | 20.2 | 120 | -7.13 | 0 | 26.25 | 33.38 | 26.02 | opened
| Nom. capacity MV, MVA | 25 | 3.24 | 10.6 | 120 | -7.36 | 0 | 26.25 | 33.61
| Nom. capacity lV, MVA | 25 | 9.83 | 9.6 | 120 | 0.23 | 0 | 26.25 | 26.02
4 | SS 110/10 B. Zhirovo | 2*6,3 | 0.36 | 0.6 | 120 | -0.24 | 0 | 6.62 | 6.86 | 6.86 | opened
5 | SS 110/35/10 Basovo | 5,6+10 | 1.19 | 6.19 | 15 | -5 | 0 | 5.88 | 10.88 | 5.38 | opened
| Nom. capacity MV, MVA | 5,6+10 | 0.5 | 6 |  | -5.5 | 0 | 5.88 | 11.38
| Nom. capacity LV, MVA | 5,6+10 | 0.69 | 0.19 | 120 | 0.5 | 0 | 5.88 | 5.38
6 | SS 110/35/10 Belaya | 2*16 | 8.4 | 12 | 120 | -3.6 | 0 | 16.8 | 20.4 | 13.4 | opened
| Nom. capacity MV, MVA | 16 | 3.4 | 0 |  | 3.4 | 0 | 16.8 | 13.4
| Nom. capacity LV, MVA | 16 | 5 | 12 | 120 | -7 | 0 | 16.8 | 23.8
7 | SS 110/35/10 Bobryshovo | 2*6,3 | 1.2 | 1.3 | 120 | -0.1 | 0 | 6.62 | 6.72 | 6.02 | opened
| Nom. capacity MV, MVA | 6.3 | 0.6 |  |  | 0.6 | 0 | 6.62 | 6.02
| Nom. capacity LV, MVA | 6.3 | 0.6 | 1.3 | 120 | -0.7 | 0 | 6.62 | 7.32
8 | SS 110/10 Vinnikovo | 2,5+6,3 | 2.31 | 1.17 | 45 | 1.14 | 0 | 2.63 | 1.49 | 1.49 | opened
9 | SS 110/35/6 Volokno | 40+2*40,5 | 37.58 | 16.8 | 0 | 20.78 | 0 | 84.53 | 63.75 | 61.28 | opened
| Nom. capacity MV, MVA | 40+2*40,5 | 14.33 | 16.8 | 0 | -2.47 | 0 | 84.53 | 87
| Nom. capacity MV, MVA | 40+2*40,5 | 23.25 | 0 | 0 | 23.25 | 0 | 84.53 | 61.28
10 | SS 110/10 Vysokaya* | 2*16 | 28.27 | 3.2 | 15 | 25.07 | 0 | 16.8 | -8.27 | -8.27 | closed*
11 | SS 110/35/10 Glushkovo | 2*10 | 8.7 | 8.04 | 120 | 0.66 | 0 | 10.5 | 9.84 | 8.44 | opened
| Nom. capacity MV, MVA | 10 | 5.2 | 6.6 | 120 | -1.4 | 0 | 10.5 | 11.9
| Nom. capacity LV, MVA | 10 | 3.5 | 1.44 | 80 | 2.06 | 0 | 10.5 | 8.44
12 | SS 110/10 Gorodskaya | 2*25 | 10.4 | 0 | 0 | 10.4 | 0 | 26.25 | 15.85 | 15.85 | opened
13 | SS 110/35/10 Gorshechnoe | 10+16 | 9.41 | 6.52 | 120 | 2.89 | 0 | 10.5 | 7.61 | 7.61 | opened
| Nom. capacity MV, MVA | 10+16 | 6.13 | 6.06 |  | 0.07 | 0 | 10.5 | 10.43
| Nom. capacity LV, MVA | 10+16 | 3.28 | 0.46 | 120 | 2.82 | 0 | 10.5 | 7.68
14 | SS 110/35/10 Dmitriev | 2*10 | 7.09 | 10.4 | 120 | -3.31 | 0 | 10.5 | 13.81 | 8.43 | opened
| Nom. capacity MV, MVA | 10 | 2.02 | 7.4 |  | -5.38 | 0 | 10.5 | 15.88
| Nom. capacity LV, MVA | 10 | 5.07 | 3 | 80 | 2.07 | 0 | 10.5 | 8.43
15 | SS 110/6 Dolgie Budy | 2*10 | 0.8 | 0.5 | 120 | 0.3 | 0 | 10.5 | 10.2 | 10.2 | opened
16 | SS 110/35/10 Zolotukhino | 2*25 | 6.76 | 23.57 | 80 | -16.81 | 0 | 26.25 | 43.06 | 25.59 | opened
| Nom. capacity MV, MVA | 25 | 2.8 | 18.8 |  | -16 | 0 | 26.25 | 42.25
| Nom. capacity LV, MVA | 25 | 3.96 | 3.3 | 120 | 0.66 | 0 | 26.25 | 25.59
17 | SS 110/35/10 Kamyshi | 2*6,3 | 8.59 | 5.45 | 20 | 3.14 | 0 | 6.62 | 3.48 | 3.07 | opened
| Nom. capacity MV, MVA | 6.3 | 7 | 3.45 |  | 3.55 | 0 | 6.62 | 3.07
| Nom. capacity LV, MVA | 6.3 | 1.59 | 2 | 20 | -0.41 | 0 | 6.62 | 7.03
18 | SS 110/35/10 Kastornoe | 15+16 | 14.13 | 6.97 | 120 | 7.16 | 0 | 15.75 | 8.59 | 8.59 | opened
| Nom. capacity MV, MVA | 15+16 | 10.63 | 6.6 |  | 4.03 | 0 | 15.75 | 11.72
| Nom. capacity LV, MVA | 15+16 | 3.5 | 0.37 | 120 | 3.13 | 0 | 15.75 | 12.62
19 | SS 110/35/10 Kilikino | 2*16 | 2.53 | 6.9 | 120 | -4.37 | 0 | 16.8 | 21.17 | 18.51 | opened
| Nom. capacity MV, MVA | 16 | 2.34 | 5 |  | -2.66 | 0 | 16.8 | 19.46
| Nom. capacity LV, MVA | 16 | 0.19 | 1.9 | 120 | -1.71 | 0 | 16.8 | 18.51
20 | SS 110/35/6 Kirovskaya | 2*40 | 53.66 | 16.36 | 120 | 37.3 | 0 | 42 | 4.7 | 4.7 | opened
| Nom. capacity MV, MVA | 40 | 26.67 | 13.06 | 120 | 13.61 | 0 | 42 | 28.39
| Nom. capacity LV, MVA | 40 | 26.99 | 3.3 | 120 | 23.69 | 0 | 42 | 18.31
21 | SS 110/35/10 Klyukva | 2*16 | 3.28 | 1.2 | 120 | 2.08 | 0 | 16.8 | 14.72 | 14.72 | opened
| Nom. capacity MV, MVA | 16 | 0 |  |  | 0 | 0 | 16.8 | 16.8
| Nom. capacity LV, MVA | 16 | 3.28 | 1.2 | 120 | 2.08 | 0 | 16.8 | 14.72
22 | SS 110/10 Kompressornaya | 2*40 | 1.11 | 0 | 0 | 1.11 | 0 | 42 | 40.89 | 40.89 | opened
23 | SS 110/35/10 Konyshevka | 10+16 | 9.06 | 8 | 120 | 1.06 | 0 | 10.5 | 9.44 | 9.44 | opened
| Nom. capacity MV, MVA | 10+16 | 6.94 | 5.9 |  | 1.04 | 0 | 10.5 | 9.46
| Nom. capacity LV, MVA | 10+16 | 2.12 | 2.1 |  | 0.02 | 0 | 10.5 | 10.48
24 | SS 110/10 Kotelnaya | 10+25 | 7.8 | 2.1 | 0 | 5.7 | 0 | 10.5 | 4.8 | 4.8 | opened
25 | SS 110/35/10 Kshen | 2*10 | 8.73 | 6.63 | 10 | 2.1 | 0 | 10.5 | 8.4 | 6.59 | opened
| Nom. capacity MV, MVA | 10 | 4.25 | 6.06 |  | -1.81 | 0 | 10.5 | 12.31
| Nom. capacity LV, MVA | 10 | 4.48 | 0.57 | 120 | 3.91 | 0 | 10.5 | 6.59
26 | SS 110/6 Lesnaya | 2*40 | 2.37 | 0 | 0 | 2.37 | 0 | 42 | 39.63 | 39.63 | opened
27 | SS 110/35/10 Lgov | 2*25 | 13.14 | 4 | 120 | 9.14 | 0 | 26.25 | 17.11 | 3.02 | opened
| Nom. capacity MV, MVA | 25 | 1.66 |  |  | 1.66 | 0 | 10.5 | 8.84
| Nom. capacity LV, MVA | 25 | 11.48 | 4 | 120 | 7.48 | 0 | 10.5 | 3.02
28 | SS 110/35/10 Lukashevka | 2*16 | 8.27 | 10.6 | 120 | -2.33 | 0 | 16.8 | 19.13 | 17.03 | opened
| Nom. capacity MV, MVA | 16 | 5.07 | 5.3 |  | -0.23 | 0 | 16.8 | 17.03
| Nom. capacity LV, MVA | 16 | 3.2 | 5.3 | 120 | -2.1 | 0 | 16.8 | 18.9
29 | SS 110/35/10 Lyubostan | 6,3+10 | 5.6 | 13.1 | 120 | -7.5 | 0 | 6.62 | 14.12 | 7.32 | opened
| Nom. capacity MV, MVA | 6,3+10 | 5 | 11.8 |  | -6.8 | 0 | 6.62 | 13.42
| Nom. capacity LV, MVA | 6,3+10 | 0.6 | 1.3 |  | -0.7 | 0 | 6.62 | 7.32
30 | SS 110/35/6 Manturovo | 2*16 | 6.58 | 9.35 | 10 | -2.77 | 0 | 16.8 | 19.57 | 16.86 | opened
| Nom. capacity MV, MVA | 16 | 6.38 | 9.09 |  | -2.71 | 0 | 16.8 | 19.51
| Nom. capacity LV, MVA | 16 | 0.2 | 0.26 | 120 | -0.06 | 0 | 16.8 | 16.86
31 | SS 110/35/10 8th Marta | 6,3+10 | 7.07 | 9.6 | 120 | -2.53 | 0 | 6.62 | 9.15 | 7.41 | opened
| Nom. capacity MV, MVA | 6,3+10 | 5.81 | 6.6 | 120 | -0.79 | 0 | 6.62 | 7.41
| Nom. capacity LV, MVA | 6,3+10 | 1.26 | 3 | 45 | -1.74 | 0 | 6.62 | 8.36
32 | SS 110/10 Martovskaya | 2*6,3 | 0.74 | 0.55 | 120 | 0.19 | 0 | 6.62 | 6.43 | 6.43 | opened
33 | SS 110/35/10 Maryino | 10+25 | 6.15 | 8.11 | 120 | -1.96 | 0 | 10.5 | 12.46 | 11.27 | opened
| Nom. capacity MV, MVA | 10+25 | 3.71 | 4.9 |  | -1.19 | 0 | 10.5 | 11.69
| Nom. capacity LV, MVA | 10+25 | 2.44 | 3.21 |  | -0.77 | 0 | 10.5 | 11.27
34 | SS 110/35/10 Medvenka | 2*10 | 5.95 | 19.22 | 120 | -13.27 | 0 | 10.5 | 23.77 | 8.74 | opened
| Nom. capacity MV, MVA | 10 | 2.07 | 17.1 |  | -15.03 | 0 | 10.5 | 25.53
| Nom. capacity LV, MVA | 10 | 3.88 | 2.12 | 120 | 1.76 | 0 | 10.5 | 8.74
35 | SS 110/6 Neftyanaya | 2*10 | 0.28 |  |  | 0.28 | 0 | 10.5 | 10.22 | 10.22 | opened
36 | SS 110/35/10 Oboyan | 16 + 25 | 16.1 | 26.86 | 120 | -10.76 | 0 | 16.8 | 27.56 | 12.16 | opened
| Nom. capacity MV, MVA | 16 + 25 | 2 | 17.4 | 0 | -15.4 | 0 | 16.8 | 32.2
| Nom. capacity LV, MVA | 16 + 25 | 14.1 | 9.46 |  | 4.64 | 0 | 16.8 | 12.16
37 | SS 110/35/10 Oktyabrskaya | 2*16 | 8.62 | 15.5 | 120 | -6.88 | 0 | 16.8 | 23.68 | 14.72 | opened
| Nom. capacity MV, MVA | 16 | 5.54 | 14.5 |  | -8.96 | 0 | 16.8 | 25.76
| Nom. capacity LV, MVA | 16 | 3.08 | 1 | 120 | 2.08 | 0 | 16.8 | 14.72
38 | SS 110/35/10 Olkhovka | 2*6,3 | 1.92 | 6.31 | 120 | -4.39 | 0 | 6.62 | 11.01 | 7.71 | opened
| Nom. capacity MV, MVA | 6.3 | 1.7 | 5 | 120 | -3.3 | 0 | 6.62 | 9.92
| Nom. capacity LV, MVA | 6.3 | 0.22 | 1.31 | 120 | -1.09 | 0 | 6.62 | 7.71
39 | SS 110/10 Paniki | 2*2,5 | 0.79 | 0.1 | 120 | 0.69 | 0 | 2.63 | 1.94 | 1.94 | opened
40 | SS 110/35/10 Peny | 2*16,0 | 9.63 | 6.9 | 120 | 2.73 | 0 | 16.8 | 14.07 | 14.07 | opened
| Nom. capacity MV, MVA | 16 | 4.37 | 3.5 |  | 0.87 | 0 | 16.8 | 15.93
| Nom. capacity LV, MVA | 16 | 5.26 | 3.4 | 120 | 1.86 | 0 | 16.8 | 14.94
41 | SS 110/35/10 Pribor | 2*25 | 32.12 | 6.5 | 0 | 25.62 | 0 | 26.25 | 0.63 | 0.63 | opened
| Nom. capacity MV, MVA | 25 | 0 |  |  | 0 | 0 | 26.25 | 26.25
| Nom. capacity LV, MVA | 25 | 32.12 | 6.5 | 0 | 25.62 | 0 | 26.25 | 0.63
42 | SS 110/10 Progress | 2*63 | 23.2 | 0 | 0 | 23.2 | 0 | 66.2 | 43 | 43 | opened
43 | SS 110/10 Poultry plant | 6,3+10 | 5.92 | 0 | 0 | 5.92 | 0 | 6.62 | 0.7 | 0.7 | opened
44 | SS 110/35/10 R. Budy | 2*10,0 | 3.4 | 15.7 | 120 | -12.3 | 0 | 10.5 | 22.8 | 15.5 | opened
| Nom. capacity MV, MVA | 10 | 2 | 9.3 |  | -7.3 | 0 | 10.5 | 17.8
| Nom. capacity LV, MVA | 10 | 1.4 | 6.4 |  | -5 | 0 | 10.5 | 15.5
45 | SS 110/35/10 Razinkovo | 6,3+10 | 2.9 | 21.4 | 45 | -18.5 | 0 | 6.62 | 25.12 | 9.27 | opened
| Nom. capacity MV, MVA | 6,3+10 | 1.95 | 17.8 |  | -15.85 | 0 | 6.62 | 22.47
| Nom. capacity LV, MVA | 6,3+10 | 0.95 | 3.6 | 45 | -2.65 | 0 | 6.62 | 9.27
46 | SS 110/35/10 Rudnaya | 2*31,5 | 20.09 | 3.25 | 10 | 16.84 | 0 | 33.1 | 16.26 | 16.26 | opened
| Nom. capacity MV, MVA | 31.5 | 14.23 | 1.7 |  | 12.53 | 0 | 33.1 | 20.57
| Nom. capacity LV, MVA | 31.5 | 5.86 | 1.55 | 120 | 4.31 | 0 | 33.1 | 28.79
47 | SS 110/35/10 Rylsk | 16+25 | 18.95 | 11 | 120 | 7.95 | 0 | 16.8 | 8.85 | 8.85 | opened
| Nom. capacity MV, MVA | 16+25 | 12.9 | 7 |  | 5.9 | 0 | 16.8 | 10.9
| Nom. capacity LV, MVA | 16+25 | 6.05 | 4 | 120 | 2.05 | 0 | 16.8 | 14.75
48 | SS 110/10 Solovyinaya | 2*25 | 6.91 | 0 | 0 | 6.91 | 0 | 26.25 | 19.34 | 19.34 | opened
49 | SS 110/10 STK | 2*10 | 1.91 | 0 | 0 | 1.91 | 0 | 10.5 | 8.59 | 8.59 | opened
50 | SS 110/10 Studenok | 2*6,3 | 3.62 | 0.7 | 120 | 2.92 | 0 | 6.62 | 3.7 | 3.7 | opened
51 | SS 110/35/10 Sudzha | 2*25 | 16.5 | 29 | 120 | -12.5 | 0 | 26.25 | 38.75 | 28.05 | opened
| Nom. capacity MV, MVA | 25 | 6.4 | 17.1 |  | -10.7 | 0 | 26.25 | 36.95
| Nom. capacity LV, MVA | 25 | 10.1 | 11.9 |  | -1.8 | 0 | 26.25 | 28.05
52 | SS 110/35/10 Schyotmash | 2*25 | 13.6 | 0 | 0 | 13.6 | 0 | 26.25 | 12.65 | 12.65 | opened
| Nom. capacity MV, MVA | 25 | 3.9 |  |  | 3.9 | 0 | 26.25 | 22.35
| Nom. capacity LV, MVA | 25 | 9.7 | 0 | 0 | 9.7 | 0 | 26.25 | 16.55
53 | SS 110/35/10 Tyotkino | 2*10 | 5.51 | 3.44 | 120 | 2.07 | 0 | 10.5 | 8.43 | 7.63 | opened
| Nom. capacity MV, MVA | 10 | 1.2 | 2 |  | -0.8 | 0 | 10.5 | 11.3
| Nom. capacity LV, MVA | 10 | 4.31 | 1.44 |  | 2.87 | 0 | 10.5 | 7.63
54 | SS 110/35/10 Tim | 6,3+16 | 5.7 | 9.59 | 120 | -3.89 | 0 | 6.62 | 10.51 | 5.02 | opened
| Nom. capacity MV, MVA | 6,3+16 | 3.6 | 9.09 |  | -5.49 | 0 | 6.62 | 12.11
| Nom. capacity LV, MVA | 6,3+16 | 2.1 | 0.5 | 120 | 1.6 | 0 | 6.62 | 5.02
55 | SS 110/35/10 Uyutnoe | 10+16 | 1.01 | 0.5 | 120 | 0.51 | 0 | 10.5 | 9.99 | 9.83 | opened
| Nom. capacity MV, MVA | 10+16 | 0.67 |  |  | 0.67 | 0 | 10.5 | 9.83
| Nom. capacity LV, MVA | 10+16 | 0.34 | 0.5 | 120 | -0.16 | 0 | 10.5 | 10.66
56 | SS 110/35/10 Fatezh | 2*16 | 6.32 | 17.4 | 120 | -11.08 | 0 | 16.8 | 27.88 | 17.08 | opened
| Nom. capacity MV, MVA | 16 | 2 | 12.8 |  | -10.8 | 0 | 16.8 | 27.6
| Nom. capacity LV, MVA | 16 | 4.32 | 4.6 | 120 | -0.28 | 0 | 16.8 | 17.08
57 | SS 110/35/10 Fosforitnaya | 2*25 | 5.44 | 12.34 | 120 | -6.9 | 0 | 26.25 | 33.15 | 24.41 | opened
| Nom. capacity MV, MVA | 25 | 3.38 | 12.12 |  | -8.74 | 0 | 26.25 | 34.99
| Nom. capacity LV, MVA | 25 | 2.06 | 0.22 | 10 | 1.84 | 0 | 26.25 | 24.41
58 | SS 110/35/10 Khomutovka | 7,5+10 | 5.69 | 6.3 | 80 | -0.61 | 0 | 7.88 | 8.49 | 5.32 | opened
| Nom. capacity MV, MVA | 7,5+10 | 0.73 | 3.9 |  | -3.17 | 0 | 7.88 | 11.05
| Nom. capacity LV, MVA | 7,5+10 | 4.96 | 2.4 | 80 | 2.56 | 0 | 7.88 | 5.32
59 | SS 110/35/10 Cheremisinovo | 2*16 | 6.15 | 9.38 | 10 | -3.23 | 0 | 16.8 | 20.03 | 15.06 | opened
| Nom. capacity MV, MVA | 16 | 4.12 | 9.09 |  | -4.97 | 0 | 16.8 | 21.77
| Nom. capacity LV, MVA | 16 | 2.03 | 0.29 | 120 | 1.74 | 0 | 16.8 | 15.06
60 | SS 110/35/10 Cheremoshki | 2*6,3 | 3.34 | 8.25 | 120 | -4.91 | 0 | 6.62 | 11.53 | 7.09 | opened
| Nom. capacity MV, MVA | 6.3 | 2.56 | 7 |  | -4.44 | 0 | 6.62 | 11.06
| Nom. capacity LV, MVA | 6.3 | 0.78 | 1.25 | 129 | -0.47 | 0 | 6.62 | 7.09
61 | SS 110/35/10 Shumakovo | 2*10 | 4.4 | 13.73 | 120 | -9.33 | 0 | 10.5 | 19.83 | 12.03 | opened
| Nom. capacity MV, MVA | 10 | 3.4 | 11.2 |  | -7.8 | 0 | 10.5 | 18.3
| Nom. capacity LV, MVA | 10 | 1 | 2.53 | 120 | -1.53 | 0 | 10.5 | 12.03
62 | SS 110/35/10 Shchigry | 2*25 | 11.28 | 12.9 | 120 | -1.62 | 0 | 26.5 | 28.12 | 21.55 | opened
| Nom. capacity MV, MVA | 25 | 5.55 | 12.12 |  | -6.57 | 0 | 26.5 | 33.07
| Nom. capacity LV, MVA | 25 | 5.73 | 0.78 | 120 | 4.95 | 0 | 26.5 | 21.55
63 | SS 110/35/10 Yastrebovka | 7,5+10 | 2.56 | 6.31 | 10 | -3.75 | 0 | 7.88 | 11.63 | 6.95 | opened
| Nom. capacity MV, MVA | 7,5+10 | 1.38 | 6.06 |  | -4.68 | 0 | 7.88 | 12.56
| Nom. capacity LV, MVA | 7,5+10 | 1.18 | 0.25 | 10 | 0.93 | 0 | 7.88 | 6.95
64 | SS 35/10 Amosovka | 2*2,5 | 0.31 | 0.2 | 120 | 0.11 | 0 | 2.63 | 2.52 | 2.52 | opened
65 | SS 35/10 Afanasyevka (SPS) | 1,6+2,5 | 0.5 | 0.37 | 120 | 0.13 | 0 | 1.68 | 1.55 | 1.55 | opened
66 | SS 35/10 B.Soldatskoe 2 | 2*4 | 1.4 | 1.1 | 80 | 0.3 | 0 | 4.2 | 3.9 | 3.9 | opened
67 | SS 35/10 B.Zmeinets | 2*1,6 | 0.23 | 1.43 | 120 | -1.2 | 0 | 1.68 | 2.88 | 2.88 | opened
68 | SS 35/10 Bezlesnaya | 2*4 | 1.19 | 6.1 | 0 | -4.91 | 0 | 4.2 | 9.11 | 9.11 | opened
69 | SS 35/10 Bereza | 1,0+2,5 | 0.49 | 0.15 | 120 | 0.34 | 0 | 1.05 | 0.71 | 0.71 | opened
70 | SS 35/10 Blagodat | 2,5+4 | 0.99 | 0.29 | 120 | 0.7 | 0 | 2.63 | 1.93 | 1.93 | opened
71 | SS 35/10 Bykanovo | 2*2,5 | 0.5 | 0.41 | 120 | 0.09 | 0 | 2.63 | 2.54 | 2.54 | opened
72 | SS 35/10 V. Lyubazh | 4+10 | 1.17 | 0.4 | 120 | 0.77 | 0 | 4.2 | 3.43 | 3.43 | opened
73 | SS 35/10 Vesyoloe | 2*1,6 | 0.8 | 0.22 | 120 | 0.58 | 0 | 1.68 | 1.1 | 1.1 | opened
74 | SS 35/10 Volobuevka | 2,5+4 | 0.57 | 0.46 | 120 | 0.11 | 0 | 2.63 | 2.52 | 2.52 | opened
75 | SS 35/10 Voropaevo | 2*4 | 0.87 | 0 | 0 | 0.87 | 0 | 4.2 | 3.33 | 3.33 | opened
76 | SS 35/10 Vostochnaya | 2*6,3 | 4.13 | 0.46 | 120 | 3.67 | 0 | 6.62 | 2.95 | 2.95 | opened
77 | SS 35/10 Vygornoe | 2*2,5 | 1.22 | 0.51 | 120 | 0.71 | 0 | 2.63 | 1.92 | 1.92 | opened
78 | SS 35/10 Gastomlya | 2*1,6 | 0.3 | 0.17 | 120 | 0.13 | 0 | 1.68 | 1.55 | 1.55 | opened
79 | SS 35/10 Gorodok | 2*4 | 1.6 | 0.7 | 45 | 0.9 | 0 | 4.2 | 3.3 | 3.3 | opened
80 | SS 35/10 Guevo | 2*2,5 | 1.2 | 1.69 | 20 | -0.49 | 0 | 2.63 | 3.12 | 3.12 | opened
81 | SS 35/10 Dolzhenkovo | 2*1,6 | 0.4 | 0.38 | 120 | 0.02 | 0 | 1.68 | 1.66 | 1.66 | opened
82 | SS 35/6 Dukhovets | 2,5+4 | 3.33 | 3.5 | 0 | -0.17 | 0 | 2.63 | 2.8 | 2.8 | opened
83 | SS 35/10 Zhernovets | 2*2,5 | 0.4 | 0.26 | 120 | 0.14 | 0 | 2.63 | 2.49 | 2.49 | opened
84 | SS 35/6 Zapadnaya | 2*10 | 12.57 | 2.5 | 0 | 10.07 | 0 | 10.5 | 0.43 | 0.43 | opened
85 | SS 35/10 Zolotukhinskaya KRS | 2*4 | 1.1 | 1.67 | 0 | -0.57 | 0 | 4.2 | 4.77 | 4.77 | opened
86 | SS 35/10 Zuevka | 1,6+2,5 | 0.9 | 0.93 | 45 | -0.03 | 0 | 1.68 | 1.71 | 1.71 | opened
87 | SS 35/10 Ivanino | 2*6,3 | 2.19 | 2.69 | 80 | -0.5 | 0 | 6.62 | 7.12 | 7.12 | opened
88 | SS 35/10 Kalinovka | 1,8+2,5 | 0.68 | 0.5 | 120 | 0.18 | 0 | 1.89 | 1.71 | 1.71 | opened
89 | SS 35/10 Kirilovka | 2*1,6 | 0.29 | 0.52 | 120 | -0.23 | 0 | 1.68 | 1.91 | 1.91 | opened
90 | SS 35/6 Kislinskaya | 2*10 | 16.7 | 6.25 | 20 | 10.45 | 0 | 10.5 | 0.05 | 0.05 | opened
91 | SS 35/10 Fodder plant | 4+6,3 | 0.29 | 0 | 0 | 0.29 | 0 | 4.2 | 3.91 | 3.91 | opened
92 | SS 35/10 Mixed fodder plant | 2*6,3 | 3.31 | 0.21 | 120 | 3.1 | 0 | 6.62 | 3.52 | 3.52 | opened
93 | SS 35/10 Kommunalnaya | 3,2+4 | 2.66 | 1.14 | 80 | 1.52 | 0 | 3.36 | 1.84 | 1.84 | opened
94 | SS 35/10 Korenevo | 4+6,3 | 3.45 | 2.7 | 80 | 0.75 | 0 | 4.2 | 3.45 | 3.45 | opened
95 | SS 35/10 Kremyanoe | 2,5+4 | 0.41 | 0.24 | 120 | 0.17 | 0 | 2.63 | 2.46 | 2.46 | opened
96 | SS 35/10 Krupets | 1,8+2,5 | 1.6 | 0.42 | 120 | 1.18 | 0 | 1.89 | 0.71 | 0.71 | opened
97 | SS 35/10 Kulbaki | 2*2,5 | 0.88 | 0.6 | 120 | 0.28 | 0 | 2.63 | 2.35 | 2.35 | opened
98 | SS 35/10 Kultprosvet | 2*2,5 | 0.18 | 0.17 | 120 | 0.01 | 0 | 2.63 | 2.62 | 2.62 | opened
99 | SS 35/10 Kurchatov | 2*10 | 4.85 | 4.5 | 80 | 0.35 | 0 | 10.5 | 10.15 | 10.15 | opened
100 | SS 35/10 Kutok | 2*2,5 | 0.17 | 0.05 | 120 | 0.12 | 0 | 2.63 | 2.51 | 2.51 | opened
101 | SS 35/10 Linets | 2*2,5 | 0.67 | 0.25 | 120 | 0.42 | 0 | 2.63 | 2.21 | 2.21 | opened
102 | SS 35/10 Luch | 2*6,3 | 2.83 | 0.23 | 120 | 2.6 | 0 | 6.62 | 4.02 | 4.02 | opened
103 | SS 35/10 Lyubimovka-2 | 2*4 | 0.75 | 1.59 | 80 | -0.84 | 0 | 4.2 | 5.04 | 5.04 | opened
104 | SS 35/10 Matveevka | 2*2,5 | 0.67 | 0.08 | 120 | 0.59 | 0 | 2.63 | 2.04 | 2.04 | opened
105 | SS 35/10 Mayak | 2*2,5 | 0.41 | 0.3 | 120 | 0.11 | 0 | 2.63 | 2.52 | 2.52 | opened
106 | SS 35/10 Mikhailovka | 4+6,3 | 2.15 | 1.7 | 80 | 0.45 | 0 | 4.2 | 3.75 | 3.75 | opened
107 | SS 35/10 Murynovka | 2*4 | 0.63 | 0.3 | 120 | 0.33 | 0 | 4.2 | 3.87 | 3.87 | opened
108 | SS 35/10 N. Borki | 2*2,5 | 0.5 | 0.63 | 120 | -0.13 | 0 | 2.63 | 2.76 | 2.76 | opened
109 | SS 35/10 Nikolskaya | 1,6+1,8 | 0.36 | 0.03 | 80 | 0.33 | 0 | 1.68 | 1.35 | 1.35 | opened
110 | SS 35/10 Novaya | 2*2,5 | 1.08 | 0.4 | 120 | 0.68 | 0 | 2.63 | 1.95 | 1.95 | opened
111 | SS 35/10 Orekhovo | 2*2,5 | 0.73 | 0.19 | 120 | 0.54 | 0 | 2.63 | 2.09 | 2.09 | opened
112 | SS 35/10 Orlovka | 2*2,5 | 0.17 | 0.52 | 120 | -0.35 | 0 | 2.63 | 2.98 | 2.98 | opened
113 | SS 35/10 Osotskoe | 2*2,5 | 0.19 | 0.2 | 120 | -0.01 | 0 | 2.63 | 2.64 | 2.64 | opened
114 | SS 35/10 Okhochevka | 4+6,3 | 1.27 | 0.74 | 120 | 0.53 | 0 | 4.2 | 3.67 | 3.67 | opened
115 | SS 35/10 Panino | 2*2,5 | 0.26 | 0.11 | 80 | 0.15 | 0 | 2.63 | 2.48 | 2.48 | opened
116 | SS 35/10 Pervoavgustovka | 2,5+3,2 | 0.74 | 0.52 | 120 | 0.22 | 0 | 2.63 | 2.41 | 2.41 | opened
117 | SS 35/10 Petrinka | 2,5+4 | 1.1 | 0.3 | 120 | 0.8 | 0 | 2.63 | 1.83 | 1.83 | opened
118 | SS 35/10 Platava | 2*2,5 | 1.07 | 0.26 | 120 | 0.81 | 0 | 2.63 | 1.82 | 1.82 | opened
119 | SS 35/10 Pogozhee | 2*1,6 | 0.23 | 0.46 | 120 | -0.23 | 0 | 1.68 | 1.91 | 1.91 | opened
120 | SS 35/10 Porechnoe | 2*4 | 0.5 | 1.16 | 120 | -0.66 | 0 | 4.2 | 4.86 | 4.86 | opened
121 | SS 35/10 Pochepnoe | 2*6,3 | 0.13 | 0.08 | 120 | 0.05 | 0 | 6.62 | 6.57 | 6.57 | opened
122 | SS 35/10 Prigorodnoe | 2*2,5 | 0.52 | 0.3 | 80 | 0.22 | 0 | 2.63 | 2.41 | 2.41 | opened
123 | SS 35/10 Pselets | 2*1,6 | 0.2 | 0.24 | 120 | -0.04 | 0 | 1.68 | 1.72 | 1.72 | opened
124 | SS 35/10 Puzachi | 1,6+4 | 0.4 | 0.43 | 120 | -0.03 | 0 | 1.68 | 1.71 | 1.71 | opened
125 | SS 35/10 Pushkarnoe | 2*2,5 | 0.8 | 0.32 | 120 | 0.48 | 0 | 2.625 | 2.145 | 2.145 | opened
126 | SS 35/10 R.Kolodets | 2*2,5 | 0.6 | 0.44 | 120 | 0.16 | 0 | 2.625 | 2.465 | 2.465 | opened
127 | SS 35/10 Razvetye | 2*4 | 2.38 | 1.03 | 120 | 1.35 | 0 | 4.2 | 2.85 | 2.85 | opened
128 | SS 35/10 V. Reutets | 2*4 | 0.28 | 0.11 | 120 | 0.17 | 0 | 4.2 | 4.03 | 4.03 | opened
129 | SS 35/10 Rozhdestvenka | 2*1,6 | 0.3 | 0.29 | 120 | 0.01 | 0 | 1.68 | 1.67 | 1.67 | opened
130 | SS 35/10 Rubilnik | 2*2,5 | 0.78 | 1.18 | 80 | -0.4 | 0 | 2.625 | 3.025 | 3.025 | opened
131 | SS 35/10 Ryzhkovo | 2*1,6 | 0.23 | 0.08 | 20 | 0.15 | 0 | 1.68 | 1.53 | 1.53 | opened
132 | SS 35/10 Sapogovo | 2*2,5 | 1.57 | 0.6 | 20 | 0.97 | 0 | 2.63 | 1.66 | 1.66 | opened
133 | SS 35/10 Svoboda-selskaya | 2*6,3 | 4.01 | 2.25 | 80 | 1.76 | 0 | 6.615 | 4.855 | 4.855 | opened
134 | SS 35/10 Selektsionnaya | 2*4 | 1.56 | 1.4 | 45 | 0.16 | 0 | 4.2 | 4.04 | 4.04 | opened
135 | SS 35/10 Semyonovka | 2*2,5 | 0.5 | 0 | - | 0.5 | 0 | 2.625 | 2.125 | 2.125 | opened
136 | SS 35/10 Seed plant | 2*2,5 | 0.6 | 0.6 | 120 | 0 | 0 | 2.63 | 2.63 | 2.63 | opened
137 | SS 35/10 Snagost | 2*4 | 1.26 | 0.05 | 10 | 1.21 | 0 | 4.2 | 2.99 | 2.99 | opened
138 | SS 35/10 SOM | 1,6+4 | 1.56 | 0.08 | 10 | 1.48 | 0 | 1.68 | 0.2 | 0.2 | opened
139 | SS 35/10 Sosnovy Bor | 3,2+4 | 0.69 | 0.69 | 120 | 0 | 0 | 3.36 | 3.36 | 3.36 | opened
140 | SS 35/10 Stakanovo | 2*2,5 | 1.23 | 0.58 | 80 | 0.65 | 0 | 2.625 | 1.975 | 1.975 | opened
141 | SS 35/10 Starkovo | 2*1,6 | 0.43 | 0.2 | 80 | 0.23 | 0 | 1.68 | 1.45 | 1.45 | opened
142 | SS 35/10 Starshee | 2*1,6 | 0.31 | 0.2 | 120 | 0.11 | 0 | 1.68 | 1.57 | 1.57 | opened
143 | SS 35/10 Teplitsy | 2*4 | 2.25 | 1.08 | 45 | 1.17 | 0 | 4.2 | 3.03 | 3.03 | opened
144 | SS 35/10 Turovka | 2*2,5 | 0.8 | 0.6 | 120 | 0.2 | 0 | 2.63 | 2.43 | 2.43 | opened
145 | SS 35/10 Uspenka | 2*2,5 | 1.19 | 1 | 80 | 0.19 | 0 | 2.63 | 2.44 | 2.44 | opened
146 | SS 35/6 Tsentralnaya | 2*25 | 24.9 | 5 | 10 | 19.9 | 0 | 26.25 | 6.35 | 6.35 | opened
147 | SS 35/10 Chermoshnoe | 2*2,5 | 0.4 | 0.5 | 120 | -0.1 | 0 | 4.2 | 4.3 | 4.3 | opened
148 | SS 35/10 Shatalovka | 2,5+4 | 0.31 | 0.21 | 80 | 0.1 | 0 | 2.625 | 2.525 | 2.525 | opened
149 | SS 35/10 Shipy | 2*2,5 | 0.2 | 0.3 | 120 | -0.1 | 0 | 2.625 | 2.725 | 2.725 | opened
150 | SS 35/10 Elevator | 4+6,3 | 2.21 | 0.6 | 120 | 1.61 | 0 | 4.2 | 2.59 | 2.59 | opened
151 | SS 35/10 Yugo-Zapadnaya | 2*10 | 9.28 | 4.7 | 80 | 4.58 | 0 | 10.5 | 5.92 | 5.92 | opened
152 | SS 35/10 Plant of reinforced-concrete products | 2*2,5 | 1.97 | 3.9 | 120 | -1.93 | 0 | 2.625 | 4.555 | 4.555 | opened
| TOTAL: | 3185.9 | 763.705 | 777.41 | [5 empty] | 1191.575
| deficit | [8 empty] | -8.27
| proficit | [8 empty] | 1183.31
*Note: Capacity deficit over SS Vysokaya is grounded by transfer of loads from SS Tsentralnaya and will be removed after putting into operation
РУ-10 кВ на ПС Центральная.
Deputy Director for Technical Issues -
|  | Chief Engineer | [6 empty] | A.N. Rudnevsky